## allbreakers
|  | Post black-out | Post-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510)
| breaker | -2 | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34
Chapelcross_33kV | 694 | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Chapelcross_33kV | 123 10 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 123 12 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 662 01 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 662 10 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 662 20 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 673 01 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 673 10 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed
Chapelcross_33kV | 673 20 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 675 10 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 676 01 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 676 10 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 676 20 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed
Chapelcross_33kV | 378 11 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 378 12 | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Chapelcross_33kV | 679 01 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 679 10 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 679 20 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 682 10 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 683 01 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed
Chapelcross_33kV | 683 10 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 683 20 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 692 01 | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Chapelcross_33kV | 694 12 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 694 13 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 694 22 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 694 23 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 698 01 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 698 11 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 698 12 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 698 13 | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 698 14 | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 698 15 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 698 16 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 698 21 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 698 22 | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 698 23 | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 698 24 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 698 25 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 698 26 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Chapelcross_33kV | 699 CHAP | closed | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 699 CUSTOMER | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 761 CHAP | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 761 CUSTOMER | closed | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 761 WINDFARM | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 780 11 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 780 12 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 780 13 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 780 14 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 781 11 | closed | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 781 12 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 781 CUSTOMER | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 785 21 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | 785 22 | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Chapelcross_33kV | 785 CUSTOMER | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Chapelcross_33kV | GRID 1 | closed | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_33kV | GRID 2 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Chapelcross_33kV | 691 01 | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Chapelcross_132kV | 120 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_132kV | 205 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Chapelcross_132kV | 330 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Chapelcross_132kV | 410 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Chapelcross_132kV | 500 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Chapelcross_132kV | 615 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Chapelcross_132kV | 710 | closed | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Chapelcross_132kV | 800 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Chapelcross_132kV | 915 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Chapelcross_132kV | 1005 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Chapelcross_132kV | 1105 | closed | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
ChapelcrossGretna_2 | 205 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
ChapelcrossGretna_2 | 1005 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
EweHill_Gretna | 805 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
EweHill_Gretna | GRID 1A | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
EweHill_Gretna | WG2 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
EweHill_Gretna | GRID 1B | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
EweHill_Gretna | 3L5 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
EweHill_Gretna | 2L5 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Minsca, Ewe Hill | CB01 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Minsca, Ewe Hill | CB02 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Minsca, Ewe Hill | CB04 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Gretna_132kV | 120 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Gretna_132kV | 780 | closed | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Gretna_132kV | 305 | closed | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Gretna_132kV | 680 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Gretna_132kV | 505 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Gretna_132kV | 405 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Gretna_132kV | 805 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Gretna_400kV | X442 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Gretna_400kV | X448 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
Gretna_400kV | X405 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Gretna_400kV | X230 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Gretna_400kV | X110 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
Gretna_400kV | X510 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed
Gretna_400kV | X605 | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | closed | closed
Minsca_33kV | 761 MINS WF | closed | open | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | 699 A | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | 699 B | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR_AUX#0 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR_AUX#1 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR_AUX#2 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR_AUX#3 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR_AUX#4 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR_AUX#5 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR_AUX#6 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR_AUX#7 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR_AUX#8 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR_AUX#9 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR_AUX#10 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR_AUX#11 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR_AUX#12 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR_AUX#13 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR_AUX#14 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR_AUX#15 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR_AUX#16 | closed | closed | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open | open
StevensCroft_33kV | STCR_AUX#17 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR_AUX#18 | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed
StevensCroft_33kV | STCR Loadbank | open | open | open | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed | closed