## Overview (1) (hidden)
Chapelcross GSP - Restoration plans
Option no | Description | Main Stages
1 | Sequential 33kV Restoration (Gen + Chap BB + WFs + Load) | 1 - Start anchor generator
2 - Energise Chapelcross 33 kV Busbar
3 - Energise WFs and supply WF's auxiliary load
4 - Pick up load at primary substations sequentially
5 - Restore loop supply to primary substations if exists
6 - Increase MW output from wind generation if available
2 | Simultaneous 33kV Restoration (Gen + Chap BB + WFs) + Load | 1 - Start Anchor Generator (may need reduced DER terminal voltage)
2 - Energise the whole Chapelcross 33 kV network simultaneously
3 - Pick up load at primary substations sequentially
4 - Restore loop supply to primary substations if exists
5 - Increase MW output from wind generation if available
3 | Chapelcross 132/33kV Tx (3A - sequential incl Ecclefecan, 3B sequential excl Ecclfecan, 3C Simultaneous incl Ecclfechan, 3D Simultaneous excl Ecclefechan)
4 | Expand from Chapelcross 132kV to Dumfries
5 | Expand from Chapelcross 132kV to Gretna

## Overview (MF) (hidden)
Chapelcross Restoratiopn Plans
Option No | Description
1
Sequence | Main Stages
1.1 | Start anchor generator
1.2 | Energise Chapelcross 33 kV Busbar
1.3 | Energise WFs and supply WF's auxiliary load
| Scenario A | Scenario B (MD<10MW) | Scenario C (10MW<MD<15MW) | Scenario D (MD>15MW)
1.4 | Pick up load at primary substations sequentially | Pick up load at primary substations sequentially - Energise transformer only first (No Load). - Allow transformer taps to adjust (Power Source Required) - Then pick up both half of busbar including load. | Pick up load at primary substations sequentially - Energise transformer only first (No Load). - Allow transformer taps to adjust (Power Source Required) - Then pick up one half of busbar including load. - then close bus section taking on second half | Pick up load at primary substations sequentially - Energise transformer only first (No Load). - Allow transformer taps to adjust (Power Source Required) - Then pick up feeders individually.
1.5 | Restore loop supply to primary substations if exists
1.6 | Increase MW output from wind generation if available
Option No | Description
2
Sequence | Main Stages
2.1 | Start Anchor Generator (may need reduced DER terminal voltage)
2.2 | Energise Chapelcross 33 kV Busbar, WFs and supply WF's auxiliary load all simultaneously
2.3 | Same stages as option 1.4-1.6 (Including alternate scenarios A-D)

## Overview (2) (hidden)
Chapelcross Restoratiopn Plans
Primary Restoration Scearios
Scenario A | Closing 33kV Primary feeder breaker energising primary transformer including demand | Scenario E (Change to B) | Close 33kV primary feeder CB to energise T1 and back energise T2 including picking up full Primary demand
Scenario B (Change to D) (MD<10MW) | Closing 33kV Primary feeder breaker energising primary transformer (No load) - Allow transformer taps to adjust (Power Source Required) - Close trf 11kV CB to pick up full demand | Scenario F (Change to C) | Close 33kV Primary feeder No1 & No2 to energise primary trf individually with 11kV bus section open
Scenario C (Change to E) (10MW<MD<15MW) | Pick up load at primary substations sequentially - Energise transformer only first (No Load). - Allow transformer taps to adjust (Power Source Required) - Then pick up one half of busbar including load. - then close bus section taking on second half | Scenario G | Energise the following groups of primary transformers: - MiddlebieT1 & Annan T1 - Kirkbank T1, Moffat T1 & Lockerbie T1 - Langholm T2, Newcastleton T1 & Gretna T1
Scenario D (Change to F) (MD>15MW) | Pick up load at primary substations sequentially - Energise transformer only first (No Load). - Allow transformer taps to adjust (Power Source Required) - Then pick up feeders individually. | Scenario H | Energise the following groups of primary transformers: - Kirkbank T1, Moffat T1 , Lockerbie T1 & MiddlebieT1 - Langholm T2, Newcastleton T1 , Gretna T1 & Annan T2
|  |  |  | Column1 | Column2 | Column3 | Column4 | Column5
Sequence | Main Stages | Description |  |  | KIRKBANK | T1 | 5 | N/K
1 |  |  |  |  | NEWCASTLETON | T1 | 5 | N/K
1.1 | Start anchor generator | Sequential 33kV Restoration of Gen → Chap BB → WFs → trf & Load/trf → load. |  |  | MOFFAT | T1 | 7.5 | N/K
1.2 | Energise Chapelcross 33 kV Busbar |  |  |  | MIDDLEBIE | T1 | 10 | 10
1.3 | Energise WFs and supply WF's auxiliary load |  |  | CHAPELCROSS | ANNAN | T1 | 12 | 12
1.4 | The 4 scenarios, A-D, detailed in the table above should be studied then continue to next step for each |  |  |  | LANGHOLM | T1 | 12 | 12
1.5 | Restore loop supply to primary substations if exists |  |  |  | GRETNA | T2 | 24 | 24
1.6 | Increase MW output from wind generation if available |  |  |  | LOCKERBIE | T1 | 24 | 24
2
2.1 | Start Anchor Generator (may need reduced DER terminal voltage) | Simultaneous 33kV Restoration of Gen+ Chap BB + WFs. Followed by sequential restoration of demand as per Option 1.
2.2 | Energise Chapelcross 33 kV Busbar, WFs and supply WF's auxiliary load all simultaneously
2.3 | Same stages as option 1.4-1.6 (Including alternate scenarios A-D) | [5 empty] | 36.5 | 29
3 | [6 empty] | 48.5 | 51
3.1
3.2
3.3
4
4.1
4.2
4.3
5
5.1
5.2
5.3
6
6.1 | Start anchor generator | Simultaneous restoration of multiple trf (2-3 in scenario E/4 in scenario F). Followed by sequential restoration of demand as per Options 1.
6.2 | Energise Chapelcross 33kV busbar and Multiple trf at once (See scenario E-F for details). Both scenario should be studied then results from studied scenarios A-D can be applied without the need for additional studies.

## Revision History
Revision | Date | Reasons for change | Changes made by
R1 | 2020-01-24 | First release agreed with SPEN | L McVey
R2 | 2020-02-03 | Corrections made | D Gutschow
R3 | 2020-02-17 | Update plan with modified scenarios for Load Flow Option 1, and comments from SPEN. (Changes in red) Ensure consistency in use of names e.g. Steven's Croft. Updated Chapelcross 132kV in Option 3-5 due to GIS changes in Dec 2020. | D Gutschow
R4 | 2020-02-26 | Update Option 3 -5 based on updated Trfr numbering at Chapelcross | D Gutschow
R5 | 2020-03-03 | Minor corrections to options 4A regarding Dumfries 33kV | D Gutschow
R6 | 2020-05-29 | Expanded Option 5 to include all the steps for the report + added WF generation requests | D Gutschow
R7 | 2020-06-19 | Added detailed steps to Options 3A-D. Wind generation still needs to be updated | D Gutschow

## Overview
Chapelcross Restoration Plans
|  |  | Column1 | Column2 | Column3 | Column4 | Column5
Option, Main Stage | Description | Summary |  | KIRKBANK | T1 | 5 | N/K
Option 1 | Sequential 33kV Restoration |  |  | NEWCASTLETON | T1 | 5 | N/K
1 | Start anchor generator | Sequential 33kV Restoration of Steven's Croft Generator, Chapelcross Busbars, Wind farms, followed by Primary substations transformers together load, or transformers followed by load. |  | MOFFAT | T1 | 7.5 | N/K
2 | Energise Chapelcross 33 kV Busbar |  |  | MIDDLEBIE | T1 | 10 | 10
3 | Energise WFs and supply WF's auxiliary load sequentially |  | CHAPELCROSS | ANNAN | T1 | 12 | 12
4 | Scenarios A-F, detailed in the "Primary Substation Restoration Options " document, should be studied for Annan Primary |  |  | LANGHOLM | T1 | 12 | 12
5 | Study remaining primary substations using Primary Substation Restoration Option C and A
6 | Restore loop supply to primary substations if exists |  |  | GRETNA | T2 | 24 | 24
7 | Increase MW output from wind generation if available |  |  | LOCKERBIE | T1 | 24 | 24
Option 2 | Simultaneous 33kV Restoration
1 | Start Anchor Generator (may need reduced DER terminal voltage) | Simultaneous 33kV Restoration of Steven's Croft generator, Chapelcross Busbars and Wind farms. Followed by sequential restoration of demand as per Option 1.
2 | Energise Chapelcross 33 kV Busbar, WFs and supply WF's auxiliary load all simultaneously
3 | Sequential restoration of demand as per Option 1, steps 5-12 |  |  |  |  | 36.5 | 29
Option 3A | Sequential 33kV Restoration with Chapelcross Grid 1 transformer including Ecclefechan |  |  |  |  | 48.5 | 51
1 | Start anchor generator | Sequential restoration of Chapelcross 33kV busbar plus Chapelcross 132kV Grid 1 Transfomer including Ecclefechan 132kV line and transformer T1
2 | Energise Chapelcross 33 kV Busbar
3 | Energise Chapelcross 132kV Grid 1 transformerl, 132kV Ecclefechan line and Eccclefechan grid trfr
4 | Energise WFs and supply WF's auxiliary load sequentially
5 | Sequential restoration of demand as per Option 1, steps 5-12
Option 3B | Sequential 33kV Restoration with Chapelcross Grid 1 transformer excluding Ecclefechan
1 | Start anchor generator | Sequential restoration of Chapelcross 33kV busbar plus Chapelcross 132kV Grid 1 Transfomer excluding Ecclefechan 132kV line and transformer T1
2 | Energise Chapelcross 33 kV Busbar, including circuits to WFs
3 | Energise Chapelcross 132kV Grid 1 transformer - Note that Circuit breaker 710 is opened in this case to prevent energising the Ecclefechan 132kV line and T1 transformer
4 | Energise WFs and supply WF's auxiliary load sequentially
5 | Sequential restoration of demand as per Option 1, steps 5-12
Option 3C | Simultaneous 33kV Restoration with Chapelcross Grid 1 transformer including Ecclefechan
1 | Start Anchor Generator (may need reduced DER terminal voltage) | Simultaneous restoration of Chapelcross 132kV Grid 1 Transformer including Ecclefechan 132kV line and transformer T1
2 | Energise Chapelcross 33 kV Busbar including the Chapelcross 132kV grid transformer 1, and Ecclefechan 132kV line and grid transformer T1, including circuits to WFs
3 | Energise WFs and supply WF's auxiliary load sequentially
4 | Sequential restoration of demand as per Option 1, steps 5-12
Option 3D | Simultaneous 33kV Restoration with Chapelcross Grid 1 transformer excluding Ecclefechan
1 | Start Anchor Generator (may need reduced DER terminal voltage) | Simultaneous restoration of Chapelcross 132kV Grid 1 Transfomer excluding Ecclefechan 132kV line and transformer T1
2 | Energise Chapelcross 33 kV Busbar including the 132kV grid 1 transformer - Note that Circuit Breaker 710 is openend to prevent energising the Ecclefechan 132kV line and grid transformer T1, including circuits to WFs
3 | Energise WFs and supply WF's auxiliary load sequentially
4 | Sequential restoration of demand as per Option 1, steps 5-12
Option 4A | Sequential 33kV Restoration extending to Dumfries Grid 1 transformer
1 | Start anchor generator | Sequential restoration of Chapelcross 33kV busbar plus Chapelcross 132kV Grid 1 transformer including Dumfries 132kV Grid 1 transformer and Dumfries 33kV busbar
2 | Energise Chapelcross 33 kV Busbar
3 | Energise Chapelcross 132kV Grid 1 Transformer
4 | Energise Chapelcross 132kV main 1 and reserve1 bus bars
5 | Energise Dumfries No.1 Circuit
6 | Energise Dumfries 33kV bus bar
7 | Energise circuit to Dalswinton WF
8 | Energise circuit to Cargenbridge primary No.1
Option 4B | Sequential 33kV Restoration extending to Dumfries Grid 2 transformer
1 | Start anchor generator | Sequential restoration of Chapelcross 33kV busbar plus Chapelcross 132kV Grid 1 transformer including Dumfries 132kV Grid 2 transformer, Dumfries 33kV busbar
2 | Energise Chapelcross 33 kV Busbar
3 | Energise Chapelcross 132kV Grid 1 Transformer
4 | Energise Chapelcross 132kV main 1 and main 2 busbar
5 | Energise Dumfries No.2 Circuit
6 | Energise Dumfries 33kV bus bar
7 | Energise circuit to Dalswinton WF
8 | Energise circuit to Cargenbridge primary No.1
Option 5 | Sequential 33kV Restoration extending to Gretna 400kV
1 | Start anchor generator | Sequential restoration of Chapelcross 33kV busbar plus Chapelcross 132kV Grid 1 transformer including Gretna 400kV transformer and Ewe Hill 132kV WF
2 | Energise Chapelcross 33 kV Busbar
3 | Energise Chapelcross 132kV Grid 1 Transformer
4 | Energise Chapelcross 132kV main 1 and reserve1 bus bars
5 | Energise Gretna 132kV busbar
6 | Energise Gretna 400kV transformer
7 | Energise circuit to Ewe Hill 132kV WF

## CB Config Option 1
Initial Circuit Breaker Configuration - Restoration Option 1 | [13 empty] | Brkr Status
Description: | [13 empty] | OPEN
Sequential 33kV Restoration (Steven's Croft Generator + Chapelcross Busbars + WFs + Primary Substations) | [13 empty] | CLOSED
[8 empty] | status change required |  |  | status change required
Initial Circuit Breaker configuration
| Circuit Breakers |  |  |  |  | Post Blackout |  | Pre-restoration status required
Substations | Name | Busbar Name | Busbar Number | CB Number | kV | CB status | Comments | Scenario A | Scenario B | Scenario C | Scenario D | Scenario E | Scenario F
[8 empty] | Energise only one 33/11kV trfr - full load | Energise both 33/11kV trfrs - full load | Energise trfr1 - half load, then energise trfr 2 - rest of load | Energise only one trfr - then switch full load | Energise trfr1 - then switch half load, then energise trfr 2 - and switch rest of load | Energise one trfr, switch 11kV load sequentially
Chapelcross Grid 33kV Busbar | Grid 1 | CHAPA3A1 | 698 | tbc | 33 | CLOSED |  | OPEN
| Grid 2 | CHAPA3A2 | 698 | tbc | 33 | CLOSED |  | OPEN
| Annan No.1 | CHAPA3A1 | 698 | 14 | 33 | OPEN | UF trip | OPEN
| Lockerbie No.1 | CHAPA3A1 | 698 | 13 | 33 | OPEN | UF trip | OPEN
| Middlebie SWS | CHAPA3A1 | 698 | 12 | 33 | CLOSED |  | OPEN
| Gretna No.2 | CHAPA3A1 | 698 | 11 | 33 | CLOSED |  | OPEN
| Bus section |  | 698 | 01 | 33 | CLOSED |  | CLOSED
| Langholm No.2/Newcastleton | CHAPA3A2 | 698 | 21 | 33 | CLOSED |  | OPEN
| Lockerbie No.2 | CHAPA3A2 | 698 | 22 | 33 | OPEN | UF trip | OPEN
| Annan No.2 | CHAPA3A2 | 698 | 23 | 33 | OPEN | UF trip | OPEN
| Steven's Croft | CHAPA3A1 | 698 | 15 | 33 | CLOSED |  | OPEN
| Minsca WF | CHAPA3A2 | 698 | 24 | 33 | CLOSED |  | OPEN
Steven's Croft SPD S/S | Chapelcross | STCR3- | 699 | 10 | 33 | CLOSED |  | OPEN
| Steven's Croft | STCR3- | 699 | 11 | 33 | OPEN | via G59 | CLOSED
Steven's Croft Customer S/S | Step-up transformer | tbc | tbc | tbc | 33 | OPEN | i/t from SPD G59, tbc | OPEN
Annan Primary Substation 33/11kV | Annan T1 | ANAN5- | 662 | 10 | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | OPEN | OPEN | OPEN
| Annan T2 | ANAN5- | 662 | 20 | 11 | CLOSED |  | OPEN | CLOSED | CLOSED | OPEN | OPEN | OPEN
| Bus section | ANAN5- | 662 | 01 | 11 | CLOSED |  | CLOSED | CLOSED | OPEN | CLOSED | OPEN | CLOSED
| All other 11kV CBs | ANAN5- | 662 | 01 | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | OPEN
Lockerbie Switching Station 33kV | Lockerbie No.1 | LOBI3A | 694 | 12 | 33 | CLOSED |  | CLOSED
| Kirkbank/Moffat No.1 | LOBI3A | 694 | 13 | 33 | CLOSED |  | OPEN
| Lockerbie No.2 | LOBI3B | 694 | 22 | 33 | CLOSED |  | CLOSED
| Moffat No.2 | LOBI3B | 694 | 23 | 33 | CLOSED |  | OPEN
| Bus section | LOBI3- | 694 | 01 | 33 | OPEN |  | OPEN
Lockerbie Primary Substation 33/11kV | Lockerbie T1 | LOBI5- | 679 | 10 | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | OPEN | OPEN | OPEN
| Lockerbie T2 | LOBI5- | 679 | 20 | 11 | CLOSED |  | OPEN | CLOSED | CLOSED | OPEN | OPEN | OPEN
| Bus section | LOBI5- | 679 | 01 | 11 | CLOSED |  | CLOSED | CLOSED | OPEN | CLOSED | OPEN | CLOSED
| All other 11kV CBs | LOBI5- | 679 | 01 | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | OPEN
Kirkbank 33/11kV | All 11kV CBs | KIBA5- | 675 |  | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | OPEN | OPEN | OPEN
Moffat Primary Substation 33/11kV | Moffat T1 | MOFT5- | 683 | 10 | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | OPEN | OPEN | OPEN
| Moffat T2 | MOFT5- | 683 | 20 | 11 | CLOSED |  | OPEN | CLOSED | CLOSED | OPEN | OPEN | OPEN
| Bus section | MOFT5- | 683 | 01 | 11 | CLOSED |  | CLOSED | CLOSED | OPEN | CLOSED | OPEN | CLOSED
| All 11kV CBs | MOFT5- | 683 |  | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | OPEN
Middlebie 33kV Sw Stn | Chapelcross | MIBI3- | 780 | 12 | 33 | CLOSED |  | CLOSED
| Ewe Hill WF | MIBI3- | 780 | 13 | 33 | CLOSED |  | CLOSED
| Langholm No.1 | MIBI3- | 780 | 14 | 33 | CLOSED |  | OPEN
| Middlebie 33/11 | MIBI3- | 780 | 11 | 33 | CLOSED |  | OPEN
Middlebie Primary Substation 33/11kV | Middlebie T1 | MIBI3- | 780 | 10 | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | OPEN | OPEN | OPEN
| All 11kV CBs | MIBI5- | 682 |  | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | OPEN
Ewe Hill WF SPD S/S | Middlebie | EWHC3- | 781 | 12 | 33 | CLOSED |  | CLOSED
| Ewe Hill WF | EWHC3- | 781 | 11 | 33 | OPEN | via G59 | OPEN
Ewe Hill WF Customer S/S | SPD substation | tbc | tbc | tbc | 33 | OPEN | i/t from SPD G59, tbc | OPEN
Langholm 33kV | Bus section |  | 692 | 01 | 33 | OPEN |  | OPEN
Langholm Primary Substation 33/11kV | T1 | LAHO5- | 676 | 10 | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | OPEN | OPEN | OPEN
| T2 | LAHO5- | 676 | 20 | 11 | CLOSED |  | OPEN | CLOSED | CLOSED | OPEN | OPEN | OPEN
| Bus section | LAHO5- | 676 | 01 | 11 | CLOSED |  | CLOSED | CLOSED | OPEN | CLOSED | OPEN | CLOSED
| All other 11kV CBs | LAHO5- | 676 |  | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | OPEN
New Castleton Primary Substation 33/11kV | T1 | NEWC5- | 123 |  | 10 | CLOSED |  | CLOSED | CLOSED | CLOSED | OPEN | OPEN | OPEN
| All 11kV CBs | NEWC5- | 123 |  | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | OPEN
Gretna 33kV | Bus section |  | 691 | 01 | 33 | OPEN |  | OPEN
Gretna Primary Substation 33/11kV | T1 | GRNA5- | 673 | 10 | 11 | CLOSED |  | OPEN | CLOSED | CLOSED | OPEN | OPEN | OPEN
| T2 | GRNA5- | 673 | 20 | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | OPEN | OPEN | OPEN
| Bus section | GRNA5- | 673 | 01 | 11 | CLOSED |  | CLOSED | CLOSED | OPEN | CLOSED | OPEN | CLOSED
| All other 11kV CBs | GRNA5- | 673 |  | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | OPEN
Minsca WF SPD S/S | Chapelcross | MINS3- | 761 | tbc | 33 | CLOSED |  | CLOSED
| Minsca WF | MINS3- | 761 | tbc | 33 | OPEN | via G59 | OPEN
Minsca WF Customer S/S | SPD substation | tbc | tbc | tbc | 33 | OPEN | i/t from SPD G59, tbc | OPEN

## CB Config Opt 1-NM (hidden)
Initial CB configuration in Restoration Option 1
Sequential 33kV Restoration (Gen + Chap BB + WFs + Load)
status change required
| Circuit Breakers |  |  | CB Status |  |  | Comments |  | Switching required?
Substations | Name | Number | kV | Post BS | Comments | Pre-restoraton status required |  | Required
Chapelcross | Grid 1 |  | 33 | CLOSED |  | OPEN | via existing SCADA control | Open | Y
Chapelcross | Grid 2 |  | 33 | CLOSED |  | OPEN | via existing SCADA control | Open | Y
Chapelcross | Annan No.1 | 13 | 33 | OPEN | UF trip | OPEN | may want to SCADA open in case not opened | Open | Y
Chapelcross | Lockerbie No.1 | 14 | 33 | OPEN | UF trip | OPEN | may want to SCADA open in case not opened | Open | Y
Chapelcross | Middlebie SWS | 12 | 33 | CLOSED |  | OPEN | via existing SCADA control | Open | Y
Chapelcross | Gretna No.2 | 11 | 33 | CLOSED |  | OPEN | via existing SCADA control | Open
Chapelcross | Bus section | 1 | 33 | CLOSED |  | CLOSED | tbc by SCADA | Open
Chapelcross | Langholm No.2/Newcastleton | 21 | 33 | CLOSED |  | CLOSED | tbc by SCADA | Open
Chapelcross | Lockerbie No.2 | 22 | 33 | OPEN | UF trip | OPEN | may want to SCADA open in case not opened | Open
Chapelcross | Annan No.2 | 23 | 33 | OPEN | UF trip | OPEN | may want to SCADA open in case not opened | Open
Chapelcross | Minsca WF | 24 | 33 | CLOSED |  | OPEN | via existing SCADA control | Open
Stevens Croft SPD S/S | Chapelcross |  | 33 | CLOSED |  | CLOSED |  | Open | N
Stevens Croft SPD S/S | Steven's Croft |  | 33 | OPEN | via G59 | OPEN
Stevens Croft Customer S/S | SPD substation |  | 33 | OPEN | i/t from SPD G59 | OPEN | Customer's equipment
Annan 33/11kV | All 11kV CBs |  |  | OPEN |  | OPEN | Network 11kV G59 connections will be open
Lockerbie 33/11kV | Lockerbie No.1 | 12 | 33 | CLOSED |  | CLOSED
Lockerbie 33/11kV | Kirkbank/Moffat No.1 | 13 | 33 | CLOSED |  | OPEN | via existing SCADA control
Lockerbie 33/11kV | Lockerbie No.2 | 22 | 33 | CLOSED |  | CLOSED
Lockerbie 33/11kV | Moffat No.2 | 23 | 33 | CLOSED |  | CLOSED
Lockerbie 33/11kV | Bus section |  | 33 | OPEN |  | OPEN | normally open
Lockerbie 33/11kV | Grid 2 | 20 | 11 | CLOSED |  | OPEN | via existing SCADA control
Lockerbie 33/11kV | All other 11kV CBs |  | 1 | CLOSED |  | CLOSED | Network 11kV G59 connections will be open
Kirkbank 33/11kV | All 11kV CBs |  | 11 | CLOSED |  | CLOSED | Network 11kV G59 connections will be open
Moffat 33/11kV | Grid 2 | 20 | 11 | CLOSED |  | OPEN | via existing SCADA control
Moffat 33/11kV | All 11kV CBs |  | 11 | CLOSED |  | CLOSED | Network 11kV G59 connections will be open
Open
Middlebie 33kV Sw Stn | Chapelcross | 12 | 33 | CLOSED |  | CLOSED
Middlebie 33kV Sw Stn | Ewe Hill WF | 13 | 33 | CLOSED |  | CLOSED
Middlebie 33kV Sw Stn | Langholm No.1 | 14 | 33 | CLOSED |  | OPEN | via existing SCADA control
Middlebie 33kV Sw Stn | Middlebie 33/11 | 11 | 33 | CLOSED |  | OPEN | via existing SCADA control
Middlebie 33/11kV | All 11kV CBs |  | 11 | CLOSED |  | CLOSED | Network 11kV G59 connections will be open
Ewe Hill WF SPD S/S | Middlebie |  | 33 | CLOSED |  | CLOSED |  | Open | N
Ewe Hill WF SPD S/S | Ewe Hill WF |  | 33 | OPEN | via G59 | OPEN
Ewe Hill WF Customer S/S | SPD substation |  | 33 | OPEN | i/t from SPD G59 | OPEN | Customer's equipment
Langholm 33/11kV | Bus section |  | 33 | OPEN |  | OPEN | normally open
Langholm 33/11kV | Grid 2 | 20 | 11 | CLOSED |  | OPEN | via existing SCADA control
Langholm 33/11kV | All 11kV CBs |  | 11 | CLOSED |  | CLOSED | Direct & network 11kV G59 will be open
Newcastleton 33/11kV | All 11kV CBs |  | 11 | CLOSED |  | CLOSED | Direct & network 11kV G59 will be open
Gretna 33/11kV | Bus section |  | 33 | OPEN |  | OPEN | normally open
Gretna 33/11kV | Grid 1 | 10 | 11 | CLOSED |  | OPEN | via existing SCADA control
Gretna 33/11kV | All other 11kV CBs |  | 11 | CLOSED |  | CLOSED | Direct & network 11kV G59 will be open
Minsca WF SPD S/S | Chapelcross |  | 33 | CLOSED |  | CLOSED |  | Open | N
Minsca WF SPD S/S | Minsca WF |  | 33 | OPEN | via G59 | OPEN
Minsca WF Customer S/S | SPD substation |  | 33 | OPEN | i/t from SPD G59 | OPEN | Customer's equipment

## Restore Option 1 (2) (hidden)
Restoration switching - Option 1 | [17 empty] | Brkr Status
Description: | [17 empty] | OPEN
Sequential 33kV Restoration (Steven's Croft Generator + Chapelcross Busbars + WFs + Primary Substations) | [17 empty] | CLOSE
Restoration Actions
Stage | Step | Substation Name | Circuit Breaker Operation | [6 empty] | Circuit Energised |  |  | Transformers Energised |  | Block Loads |  |  |  |  | System studies results (OK vs Fail)
|  |  | Busbar Name | Busbar Number | kV | Circuit | CB Number | CB action | Comment | Description | MVA | Cumulative MVA | Name (Substation, Trfr no) | MVA | Name | Max MVA | Min MVA | PF | Maximum % of DER | Load Flow Check | Voltage & Control check | Frequency response check | Transient stability check | System studies results check
1 |  | STCR gen has energised up to SPD Steven's Croft 33kV interface CB
Start anchor DER
| 1.1 | Stevens Croft Cust S/S |  |  | 33 | Stevens Croft SPD s/s |  | CLOSE | Cust switching.Energise SPD 33 kV busbar and earthing Tx + Load bank | STCR3- - CHAPA3A1 |  |  |  | tbc
| 1.2 | Stevens Croft SPD S/S | STCR3- | 699 | 33 | Chapelcross | tbc | CLOSE | Energise 33kV cable to Chapelcross
2 | 2.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Stevens Croft 33 kV | 15 | CLOSE | Energise Chapelcross 33 kV busbars
3 |  | Restoration of Power Supply to Minsca Windfarm
| 3.1 | Chapelcross | CHAPA3A2 | 698 | 33 | Minsca WF | 24 | CLOSE | Energise circuit and Minsca SPD 33 kV busbar | CHAPA3A2 - MINS3-
| 3.2 | Minsca SPD S/S | MINS3- | 716 | 33 | Customer S/S | tbc | CLOSE | Energise customer S/S 33 kV busbar
| 3.3 | Minsca Customer S/S | tbc | tbc | 33 | 33 kV feeders | tbc | CLOSE | Energise cable feeders. Restore aux to WTGs. |  |  |  | Auxiliary transformer
No MWs from WTGs until instructed.
4 |  | Restoration of Power Supply to EWE Hill Windfarm
| 4.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Middlebie SWS | 14 | CLOSE | Energise circuit to EWE Hill WF via Middlebie SWS | CHAPA3A1 - MIBI3- MIBI3- - EWHC3-
| 4.2 | EWE Hill SPD S/S | EWHC3- | 781 | 33 | Customer S/S | tbc | CLOSE | Energise customer S/S 33 kV busbar
| 4.3 | EWE Hill Customer S/S | tbc | tbc | 33 | 33 kV feeders | tbc | CLOSE | Energise cable feeders. Restore aux to WTGs. |  |  |  | Auxiliary transformer | tbc | EWE Hill WF Aux
No MWs from WTGs until instructed.
5 |  | Restoration of Power Supply to Annan PS (3 trial options to be considered initially)
| 5.1A | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | A) Energise feeder transformer for T1 and pick up block load | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12 | Annan PS | 12.12
| 5.1B | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T2 | 20 | CLOSE | Ensure CB 20 to be closed in pre-restoration
| 5.2B | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | B) Energise feeder transformers T1&T2 and pick up block load | CHAPA3A1 - ANANT1 CHAPA3A2 - ANNAT2 |  |  | Annan T1 33/11kV Annan T2 33/11kV | 12 12 | Annan PS | 12.12
|  | Chapelcross | CHAPA3A2 | 698 | 33 | Annan No.2 | 23 | CLOSE | Restores No.2 33kV cct for security/protection purposes.
| 5.1C | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T2 | 20 | CLOSE | Ensure CB 20 closed in pre-restoration
| 5.2C | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T2 | 01 | OPEN | Run 2x11 kV sections (only viable if no closed 11kV rings)
| 5.3C | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | C) Energise feeder transformer T1 and pick up half block load | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12 | Annan PS | 6.6 tbc
| 5.4C | Chapelcross | CHAPA3A2 | 698 | 33 | Annan No.2 | 23 | CLOSE | C) Energise feeder transformer T2 and pick up half block load | CHAPA3A2 - ANANT2 |  |  | Annan T2 33/11kV | 12 | Annan PS | 6.6 tbc
6 |  | Restoration of Power Supply to Middlebie PS
| 6.1 | Middlebie SWS | MIBI3- | 780 | 33 | Middlebie No.1 | 11 | CLOSE | Energise feeder transformer and pick up block load |  |  |  | Middlebie 33/11kV | 10 | Middlebie PS | 5.24
7 |  | Restoration of Power Supply to Langholm PS
| 7.1 | Middlebie SWS | MIBI3- | 780 | 33 | Langholm No.1 | 14 | CLOSE | Energise feeder transformer for T1 and pick up block load | MIBI3- - LAHO3A |  |  | Langholm T1 33/11kV | 12 | Langholm PS | 6.35
8 |  | Restoration of Power Supply to Gretna PS
| 8.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Gretna No.2 | 11 | CLOSE | Energise feeder transformer for T2 and pick up block load | CHAPA3A1 - GRNA3B |  |  | Gretna T2 33/11kV | 12 | Gretna PS | 7.1
9 |  | Restoration of Power Supply to Newcastelton PS
| 9.1 | Chapelcross | CHAPA3A2 | 698 | 33 | Gretna No.1, Langholm No.2, and Newcastelton. | 21 | CLOSE | Energise Newcastleton T1 and pick up block load | CHAPA3A2 - X3 X3 - GRNA3A X3 - LAHO3B |  |  | Newcastelton 33/11 kV | 10 | Newcastelton PS | 1.09
10 |  | Restoration of Power Supply to Lockerbie PS
| 10.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Lockerbie No.1 | 14 | CLOSE | Energise Lockerbie T1 & No.2 33kV cct, pick up block load | CHAPA3A1 - X1 X1 - LOBI3A |  |  | Lockerbie T1 33/11kV | 24 | Lockerbie PS | 14.65
Dumfries?
11 |  | Restoration of Power Supply to Kirkbank/Moffat PS
| 11.1 | Lockerbie | LOBI3A | 694 | 33 | Kirkbank & Moffat No.1 | 13 | CLOSED | Energise 2 feeder transformer and pick up block load | LOBI3A - X4 X4 - KIBAT1 X4 - MOFTT1 |  |  | Kirkbank 33/11kV Moffat T1 33/11kV | 5 7.5 | Kirkbank PS | 1.37
Notes:
| 1) | The results from the Annan primary energising options may determine the preferred method of energising a primary.
| 2) | In reality when a primary demand block is switched in it is anticipated that a load bank will be switched out, or other DER (apart from anchor gen) will automatically help support the frequency.

## Restore Option 1
Restoration switching (Option 1): Sequential 33kV Restoration (Steven's Croft Generator + Chapelcross Busbars + WFs + Primary Substations) | [18 empty] | Brkr Status
Description: | [18 empty] | OPEN
Sequential 33kV Restoration (teven's Croft Generator + Chapelcross Busbars + WFs + Primary Substations) Primary substation restoration options: A - Energise the No.1 33/11kV trf with T1 11kV CB closed, taking on the full load at the Primary Substation (T2 11kV CB should be open). B - Energise the No.1 33/11kV trf with T1 & T2 11kV CBs closed, taking of the full load at the Primary Substation; Energising both Primary Transformers. C - Ensure the bus-section is open. Energise the No.1 33/11kV trf with T1 11kV CB closed, taking on half the load at the Primary Substation. Then, if applicable, energise the No.2 33/11kV trf (from the GSP) with T2 11kV CB closed, taking on the second half the load at the Primary Substation. D - Energise the No.1 33/11kV trf with T1 11kV CB open. Once T1 is energised, close T1 11kV CB, taking of the full load at the Primary Substation (T2 11kV CB should be open). E - Ensure the bus-section is open. Energise the No.1 33/11kV trf with T1 11kV CB open. Once T1 is energised, close T1 11kV CB taking on half the load at the Primary Substation. Then, close the bus-section taking on the second half the load at the Primary Substation. F - Energise the No.1 33/11kV trf with T1 11kV CB open. Ensure the bus-section is closed and all 11kV feeder CB's are open, then close T1 11kV CB to energise the 11kV busbar. Finally, sequentially close 11kV feeder CB's, energising the individual 11kV feeder circuits. G - Similar to A, except that only half the substation load is picked up initially by opening the 11kV BS breaker, and then after a delay closing the BS to pickup the rest of the load. | [18 empty] | CLOSE
Restoration Actions
Stage |  | Step | Substation Name | Circuit Breaker Operation | [6 empty] | Circuit Energised |  |  | Transformers Energised |  | Block Loads |  |  |  |  | System studies results (OK vs Fail)
| Transformer energisation scenario |  |  | Busbar Name | Busbar Number | kV | Circuit | CB Number | CB action | Comment | Description | MVA | Cumulative MVA | Name (Substation, Trf no) | MVA | Name | Max MVA | Min MVA | PF | Maximum % of DER | Load Flow Check | Voltage & Control check | Frequency response check | Transient stability check | System studies results check
0 |  |  | Steven's Croft generator has energised up to SPD Steven's Croft 33kV interface CB | [6 empty] | Start anchor DER
1 |  | 1 | Connecting Steven's Croft anchor generator to Chapelcross GSP
|  | 1.1 | Steven's Croft Cust S/S |  |  | 33 | Steven's Croft SPD s/s |  | CLOSE | Cust switching.Energise SPD 33 kV busbar and earthing trfr + Load bank | STCR3- - CHAPA3A1 |  |  |  | tbc
|  | 1.2 | Steven's Croft SPD S/S | STCR3- | 699 | 33 | Chapelcross | tbc | CLOSE | Energise 33kV cable to Chapelcross
2 |  | 2 | Energise Chapelcross 33kV Busbars
|  | 2.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Steven's Croft 33 kV | 15 | CLOSE | Energise Chapelcross 33 kV busbars
3 |  | 3 | Restoration of Power Supply to Minsca Windfarm
|  | 3.1 | Chapelcross | CHAPA3A2 | 698 | 33 | Minsca WF | 24 | CLOSE | Energise circuit and Minsca SPD 33 kV busbar | CHAPA3A2 - MINS3-
|  | 3.2 | Minsca SPD S/S | MINS3- | 761 | 33 | Customer S/S | tbc | CLOSE | Energise customer S/S 33 kV busbar
|  | 3.3 | Minsca Customer S/S | tbc | tbc | 33 | 33 kV feeders | tbc | CLOSE | Energise cable feeders. Restore aux supply to WTGs. |  |  |  | Auxiliary transformer
No MWs from WTGs until instructed. Need to switch WTGs from voltage control mode to power factor control mode
4 |  | 4 | Restoration of Power Supply to Ewe Hill Windfarm
|  | 4.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Middlebie SWS | 12 | CLOSE | Energise circuit to Ewe Hill WF via Middlebie SWS | CHAPA3A1 - MIBI3- MIBI3- - EWHC3-
|  | 4.2 | Ewe Hill SPD S/S | EWHC3- | 781 | 33 | Customer S/S | 11 | CLOSE | Energise customer S/S 33 kV busbar
|  | 4.3 | Ewe Hill Customer S/S | tbc | tbc | 33 | 33 kV feeders | tbc | CLOSE | Energise cable feeders. Restore aux to WTGs. |  |  |  | Auxiliary transformer | tbc | Ewe Hill WF Aux
No MWs from WTGs until instructed. Need to switch WTGs from voltage control mode to power factor control mode
5 |  | 5 | Restoration of Power Supply to Annan Primary Substation. Primary restoration options A-F considered.
| A | 5.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1 and pick up block load | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12 | Annan PS | 12.12
| B | 5.1 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T2 | 20 | CLOSE | Ensure CB 20 to be closed in pre-restoration
| B | 5.2 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformers T1 &T2 and pick up block load | CHAPA3A1 - ANANT1 CHAPA3A2 - ANNAT2 |  |  | Annan T1 33/11kV Annan T2 33/11kV | 12 12 | Annan PS | 12.12
| B | 5.3 | Chapelcross | CHAPA3A2 | 698 | 33 | Annan No.2 | 23 | CLOSE | Restores No.2 33kV cct for security/protection purposes.
Preferred Option | C | 5.1 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T2 | 20 | CLOSE | Ensure CB 20 closed in pre-restoration
| C | 5.2 | Annan PS | ANAN5- | 662 | 11 | Bus section | 01 | OPEN | Run 2x11 kV sections (only viable if no closed 11kV rings)
| C | 5.3 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer T1 and pick up half block load | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12 | Annan PS | 6.06 tbc
| C | 5.4 | Chapelcross | CHAPA3A2 | 698 | 33 | Annan No.2 | 23 | CLOSE | Energise feeder transformer T2 and pick up half block load | CHAPA3A2 - ANANT2 |  |  | Annan T2 33/11kV | 12 | Annan PS | 6.06 tbc
| D | 5.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1 | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12
| D | 5.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Full load at Annan Primary | [5 empty] | Annan PS | 12.12
| E | 5.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1 | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12
| E | 5.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Half load at Annan Primary | [5 empty] | Annan PS | 6.06 tbc
| E | 5.3 | Annan PS | ANAN5- | 662 | 11 | 11kV bus-section | 01 | CLOSE | Close bus-section and energise second half of the Primary load | [5 empty] | Annan PS | 6.06 tbc
| F | 5.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1 | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12
| F | 5.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T1 | 10 | CLOSE | Energise 11kV busbar
| F | 5.3 | Annan PS | ANAN5- | 662 | 11 | 11kV feeders | tbc | CLOSE | Take on feeders one at a time | [5 empty] | Annan PS | ?
6 | A | 6 | Restoration of Power Supply to Middlebie PS
|  | 6.1 | Middlebie SWS | MIBI3- | 780 | 33 | Middlebie No.1 | 11 | CLOSE | Energise feeder transformer and pick up block load |  |  |  | Middlebie 33/11kV | 10 | Middlebie PS | 5.24
7 | A | 7 | Restoration of Power Supply to Langholm PS
|  | 7.1 | [7 empty] | Instruct Minsca WF (43 MVA) to generate 15MW.
|  | 7.2 | Middlebie SWS | MIBI3- | 780 | 33 | Langholm No.1 | 14 | CLOSE | Energise feeder transformer for T1 and pick up block load | MIBI3- - LAHO3A |  |  | Langholm T1 33/11kV | 12 | Langholm PS | 6.35
8 | A | 8 | Restoration of Power Supply to Gretna PS
|  | 8.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Gretna No.2 | 11 | CLOSE | Energise feeder transformer for T2 and pick up block load | CHAPA3A1 - GRNA3B |  |  | Gretna T2 33/11kV | 12 | Gretna PS | 7.1
9 | A | 9 | Restoration of Power Supply to Newcastelton PS
|  | 9.1 | Chapelcross | CHAPA3A2 | 698 | 33 | Gretna No.1, Langholm No.2, and Newcastelton. | 21 | CLOSE | Energise Newcastleton T1 and pick up block load | CHAPA3A2 - X3 X3 - GRNA3A X3 - LAHO3B |  |  | Newcastelton 33/11kV Gretna T1 33/11kV Langholm T2 33/11kV | 5 in LTDS 12 12 | Newcastelton PS | 1.09
10 | C | 10 | Restoration of Power Supply to Lockerbie PS Load 1 & 2
|  | 10.1 | [7 empty] | Instruct Minsca WF (43 MVA) to increase generation to 20MW.
|  | 10.2 | [7 empty] | Instruct Ewe WF (12.63 MVA) to generate 5 MW
|  | 10.3 | Lockerbie | LOBI3- | 679 | 33 | 11 kV bus section | 01 | OPEN | Run 2 x 11kV sections (only viable if no closed rings) [Bus section be OPEN already]
|  | 10.4 | Chapelcross | CHAPA3A1 | 698 | 33 | Lockerbie No.1 | 14 | CLOSE | Energise Lockerbie T1 & Lockerbie Load 1. Pick up half block load. | CHAPA3A1 - X1 X1 - LOBI3A |  |  | Lockerbie T1 33/11kV | 24 | Lockerbie PS | =14.65 / 2
|  | 10.5 | Chapelcross | CHAPA3A2 | 698 | 33 | Lockerbie No. 2 | 22 | CLOSE | Energise Lockerbie T2 & Lockerbie Load 2. Pick uo half block load. |  |  |  | Lockerbie T1 33/11kV | 24 | Lockerbie PS | =14.65 / 2
11 | C | 11 | Restoration of Power Supply to Kirkbank/Moffat PS Load 1
|  | 11.1 | Moffat | MOFT5- | 683 | 11 | 11kV bus section | 01 | OPEN | Run 2 x 11kV sections (only viable if no closed rings) [Bus section be OPEN already] |  |  |  | Kirkbank 33/11kV Moffat T1 33/11kV | 5 7.5 | Kirkbank PS Moffat T1 | 1.37
|  | 11.2 | Lockerbie | LOBI3A | 694 | 33 | Kirkbank & Moffat No.1 | 13 | CLOSE | Energise Moffat T1 and Load 1 and pick up block load. Delay before step 12 | LOBI3A - X4 X4 - KIBAT1 X4 - MOFTT1
12 | C | 12 | Restoration of Power Supply to Moffat PS Load 2
|  | 12.1 | Lockerbie | LOBI3A | 694 | 33 | Moffat No. 2 | 23 | CLOSE | After cold load delay, energise Moffat T2 and Load 2 and pick up block load. |  |  |  | Moffat T2 33/11kV | 7.5 | Moffat T2
13 |  | 13 | Restore network to normal operating mode to improve supply security
|  | 13.1 | Annan PS | ANAN5- | 662 | 11 | 11kV bus section | 01 | CLOSE | Close bus section to improve supply security
|  | 13.2 | Lockerbie PS | LOBI3- | 679 | 11 | 11kV bus section | 01 | CLOSE | Close bus section to improve supply security
|  | 13.3 | Moffat PS | MOFT5- | 683 | 11 | 11kV bus section | 01 | CLOSE | Close bus section to improve supply security
|  | 13.4 | Langholm | LAHO5- | 676 | 11 | Langholm T2 | 20 | CLOSE | Connect T2 to improve supply security
|  | 13.5 | Gretna | GRNA5- | 673 | 11 | Gretna T1 | 10 | CLOSE | Connect T1 to improve supply security
5b |  |  | Restoration of Power Supply to Primary Substation (PS), energising the trf then taking on full load
Scenario B |  | 5.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 14 | CLOSE | Energise feeder transformer for T1 | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12
|  | 5.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Full load at Annan Primary | [5 empty] | Annan PS | 12.12
6b |  |  | Restoration of Power Supply to Middlebie PS
|  | 6.1 | Middlebie SWS | MIBI3- | 780 | 33 | Middlebie No.1 | 11 | CLOSE | Energise feeder transformer |  |  |  | Middlebie 33/11kV | 10
|  | 6.2 | Middlebie PS | MIBI5- | 682 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Full load at Middlebie Primary | [5 empty] | Middlebie PS | 5.24
7b |  |  | Restoration of Power Supply to Langholm PS
|  | 7.1 | Middlebie SWS | MIBI3- | 780 | 33 | Langholm No.1 | 14 | CLOSE | Energise feeder transformer for T1 | MIBI3- - LAHO3A |  |  | Langholm T1 33/11kV | 12
|  | 7.2 | Langholm PS | LAHO5- | 676 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Full load at Langholm Primary | [5 empty] | Langholm PS | 6.35
8b |  |  | Restoration of Power Supply to Gretna PS
|  | 8.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Gretna No.2 | 11 | CLOSE | Energise feeder transformer for T2 | CHAPA3A1 - GRNA3B |  |  | Gretna T2 33/11kV | 12
|  | 8.2 | Gretna PS | GRNA5- | 673 | 11 | 11kV busbar for T2 | 20 | CLOSE | Take on Full load at Gretna Primary | [5 empty] | Gretna PS | 7.1
9b |  |  | Restoration of Power Supply to Newcastelton PS
|  | 9.1 | Chapelcross | CHAPA3A2 | 698 | 33 | Gretna No.1, Langholm No.2, and Newcastelton. | 21 | CLOSE | Energise Newcastleton T1 | CHAPA3A2 - X3 X3 - GRNA3A X3 - LAHO3B |  |  | Newcastelton 33/11kV Gretna T1 33/11kV Langholm T2 33/11kV | 10 (5 in LTDS?) 12 12
|  | 9.2 | Newcastelton PS | NEWC5- | 123 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Full load at Newcastelton Primary | [5 empty] | Newcastelton PS | 1.09
10b |  |  | Restoration of Power Supply to Lockerbie PS
|  | 10.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Lockerbie No.1 | 14 | CLOSE | Energise Lockerbie T1 | CHAPA3A1 - X1 X1 - LOBI3A |  |  | Lockerbie T1 33/11kV | 24
|  | 10.2 | Lockerbie PS | LOBI5- | 679 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Full load at Lockerbie Primary | [5 empty] | Lockerbie PS | 15.4
11b |  |  | Restoration of Power Supply to Kirkbank/Moffat PS
|  | 11.1 | Lockerbie SWS | LOBI3A | 694 | 33 | Kirkbank & Moffat No.1 | 13 | CLOSE | Energise 2 feeder transformers | LOBI3A - X4 X4 - KIBAT1 X4 - MOFTT1 |  |  | Kirkbank 33/11kV Moffat T1 33/11kV | 5 7.5
|  | 11.2 | Kirkbank PS | KIBA5- | 675 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Full load at Kirkbank Primary | [5 empty] | Kirkbank PS | 1.9
|  | 11.3 | Moffat PS | MOFF5- | 683 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Full load at Moffat Primary | [5 empty] | Moffat PS | 3.9
5c |  |  | Restoration of Power Supply to Primary Substation (PS), energising the trf, then taking on each half of the primary busbar
| E | 5.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 14 | CLOSE | Energise feeder transformer for T1 | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12
| E | 5.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Half load at Annan Primary | [5 empty] | Annan PS | 6.06
| E | 5.3 | Annan PS | ANAN5- | 662 | 11 | 11kV bus-section | 01 | CLOSE | Close bus-section and energise second half of the Primary load | [5 empty] | Annan PS | 6.06
E
6c | E |  | Restoration of Power Supply to Middlebie PS
| E | 6.1 | Middlebie SWS | MIBI3- | 780 | 33 | Middlebie No.1 | 11 | CLOSE | Energise feeder transformer |  |  |  | Middlebie 33/11kV | 10
| E | 6.2 | Middlebie PS | MIBI5- | 682 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Full load at Middlebie Primary | [5 empty] | Middlebie PS | 5.24
E
7c | E |  | Restoration of Power Supply to Langholm PS
|  | 7.1 | Middlebie SWS | MIBI3- | 780 | 33 | Langholm No.1 | 14 | CLOSE | Energise feeder transformer for T1 | MIBI3- - LAHO3A |  |  | Langholm T1 33/11kV | 12
|  | 7.2 | Langholm PS | LAHO5- | 676 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Half load at Langholm Primary | [5 empty] | Langholm PS | 3.175
|  | 7.3 | Langholm PS | LAHO5- | 676 | 11 | 11kV bus-section | 01 | CLOSE | Close bus-section and energise second half of the Primary load | [5 empty] | Langholm PS | 3.175
8c |  |  | Restoration of Power Supply to Gretna PS
|  | 8.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Gretna No.2 | 11 | CLOSE | Energise feeder transformer for T2 | CHAPA3A1 - GRNA3B |  |  | Gretna T2 33/11kV | 12
|  | 8.2 | Gretna PS | GRNA5- | 673 | 11 | 11kV busbar for T2 | 20 | CLOSE | Take on Half load at Gretna Primary | [5 empty] | Gretna PS | 3.55
|  | 8.3 | Gretna PS | GRNA5- | 673 | 11 | 11kV bus-section | 01 | CLOSE | Close bus-section and energise second half of the Primary load | [5 empty] | Gretna PS | 3.55
9c |  |  | Restoration of Power Supply to Newcastelton PS
|  | 9.1 | Chapelcross | CHAPA3A2 | 698 | 33 | Gretna No.1, Langholm No.2, and Newcastelton. | 21 | CLOSE | Energise Newcastleton T1 | CHAPA3A2 - X3 X3 - GRNA3A X3 - LAHO3B |  |  | Newcastelton 33/11kV Gretna T1 33/11kV Langholm T2 33/11kV | 10 (5 in LTDS?) 12 12
|  | 9.2 | Newcastelton PS | NEWC5- | 123 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Full load at Newcastelton Primary | [5 empty] | Newcastelton PS | 1.09
10c |  |  | Restoration of Power Supply to Lockerbie PS
|  | 10.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Lockerbie No.1 | 14 | CLOSE | Energise Lockerbie T1 | CHAPA3A1 - X1 X1 - LOBI3A |  |  | Lockerbie T1 33/11kV | 24
|  | 10.2 | Lockerbie PS | LOBI5- | 679 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Half load at Lockerbie Primary | [5 empty] | Lockerbie PS | 7.52
|  | 10.3 | Lockerbie PS | LOBI5- | 679 | 11 | 11kV bus-section | 01 | CLOSE | Close bus-section and energise second half of the Primary load | [5 empty] | Lockerbie PS | 7.52
11c |  |  | Restoration of Power Supply to Kirkbank/Moffat PS
|  | 11.1 | Lockerbie SWS | LOBI3A | 694 | 33 | Kirkbank & Moffat No.1 | 13 | CLOSE | Energise 2 feeder transformers | LOBI3A - X4 X4 - KIBAT1 X4 - MOFTT1 |  |  | Kirkbank 33/11kV Moffat T1 33/11kV | 5 7.5
|  | 11.2 | Kirkbank PS | KIBA5- | 675 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Full load at Kirkbank Primary | [5 empty] | Kirkbank PS | 1.9
|  | 11.3 | Moffat PS | MOFF5- | 683 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Full load at Moffat Primary | [5 empty] | Moffat PS | 1.95
|  | 11.4 | Moffat PS | MOFF5- | 683 | 11 | 11kV bus-section | 01 | CLOSE | Close bus-section and energise second half of the Primary load | [5 empty] | Moffat PS | 1.95
5d |  |  | Restoration of Power Supply to Primary Substation (PS), energising the trf then taking on individual feeders
|  | 5.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 14 | CLOSE | Energise feeder transformer for T1 | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12
|  | 5.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T1 | 10 | CLOSE | Energise 11kV busbar
|  | 5.3 | Annan PS | ANAN5- | 662 | 11 | 11kV feeders |  | CLOSE | Take on feeders one at a time | [5 empty] | Annan PS | ?
6d |  |  | Restoration of Power Supply to Middlebie PS
|  | 6.1 | Middlebie SWS | MIBI3- | 780 | 33 | Middlebie No.1 | 11 | CLOSE | Energise feeder transformer |  |  |  | Middlebie 33/11kV | 10
|  | 6.2 | Middlebie PS | MIBI5- | 682 | 11 | 11kV busbar | 10 | CLOSE | Energise 11kV busbar
|  | 6.3 | Middlebie PS | MIBI5- | 682 | 11 | 11kV feeders |  | CLOSE | Take on feeders one at a time | [5 empty] | Middlebie PS | ?
7d |  |  | Restoration of Power Supply to Langholm PS
|  | 7.1 | Middlebie SWS | MIBI3- | 780 | 33 | Langholm No.1 | 14 | CLOSE | Energise feeder transformer for T1 | MIBI3- - LAHO3A |  |  | Langholm T1 33/11kV | 12
|  | 7.2 | Langholm PS | LAHO5- | 676 | 11 | 11kV busbar for T1 | 10 | CLOSE | Energise 11kV busbar
|  | 7.3 | Langholm PS | LAHO5- | 676 | 11 | 11kV feeders |  | CLOSE | Take on feeders one at a time | [5 empty] | Langholm PS | ?
8d |  |  | Restoration of Power Supply to Gretna PS
|  | 8.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Gretna No.2 | 11 | CLOSE | Energise feeder transformer for T2 | CHAPA3A1 - GRNA3B |  |  | Gretna T2 33/11kV | 12
|  | 8.2 | Gretna PS | GRNA5- | 673 | 11 | 11kV busbar | 20 | CLOSE | Energise 11kV busbar
|  | 8.3 | Gretna PS | GRNA5- | 673 | 11 | 11kV feeders |  | CLOSE | Take on feeders one at a time | [5 empty] | Gretna PS | ?
9d |  |  | Restoration of Power Supply to Newcastelton PS
|  | 9.1 | Chapelcross | CHAPA3A2 | 698 | 33 | Gretna No.1, Langholm No.2, and Newcastelton. | 21 | CLOSE | Energise Newcastleton T1 | CHAPA3A2 - X3 X3 - GRNA3A X3 - LAHO3B |  |  | Newcastelton 33/11kV Gretna T1 33/11kV Langholm T2 33/11kV | 10 (5 in LTDS?) 12 12
|  | 9.2 | Newcastelton PS | NEWC5- | 123 | 11 | 11kV busbar for T1 | 10 | CLOSE | Energise 11kV busbar
|  | 9.3 | Newcastelton PS | NEWC5- | 123 | 11 | 11kV feeders |  | CLOSE | Take on feeders one at a time | [5 empty] | Newcastelton PS | ?
10d |  |  | Restoration of Power Supply to Lockerbie PS
|  | 10.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Lockerbie No.1 | 14 | CLOSE | Energise Lockerbie T1 | CHAPA3A1 - X1 X1 - LOBI3A |  |  | Lockerbie T1 33/11kV | 24
|  | 10.2 | Lockerbie PS | LOBI5- | 679 | 11 | 11kV busbar for T1 | 10 | CLOSE | Energise 11kV busbar
|  | 10.3 | Lockerbie PS | LOBI5- | 679 | 11 | 11kV feeders |  | CLOSE | Take on feeders one at a time | [5 empty] | Lockerbie PS | ?
11d |  |  | Restoration of Power Supply to Kirkbank/Moffat PS
|  | 11.1 | Lockerbie SWS | LOBI3A | 694 | 33 | Kirkbank & Moffat No.1 | 13 | CLOSE | Energise 2 feeder transformers | LOBI3A - X4 X4 - KIBAT1 X4 - MOFTT1 |  |  | Kirkbank 33/11kV Moffat T1 33/11kV | 5 7.5
|  | 11.2 | Kirkbank PS | KIBA5- | 675 | 11 | 11kV busbar for T1 | 10 | CLOSE | Energise 11kV busbar
|  | 11.3 | Kirkbank PS | KIBA5- | 675 | 11 | 11kV feeders |  | CLOSE | Take on feeders one at a time | [5 empty] | Kirkbank PS | ?
|  | 11.4 | Moffat PS | MOFF5- | 683 | 11 | 11kV busbar for T1 | 10 | CLOSE | Energise 11kV busbar
|  | 11.5 | Moffat PS | MOFF5- | 683 | 11 | 11kV feeders |  | CLOSE | Take on feeders one at a time | [5 empty] | Moffat PS | ?
Note on B35: Dieter Gutschow: Option C is preferred over option A due to overloading of transformers due to cold load pickup

## CB Config Option 2 v1 (hidden)
Initial Circuit Breaker Configuration - Restoration Option 2 | [14 empty] | Brkr Status
Description: | [14 empty] | OPEN
Simultaneous 33kV Restoration of Gen+ Chap BB + WFs. Followed by sequential restoration of demand as per Options 1. | [10 empty] | Last values |  |  |  | CLOSED
[8 empty] | status change required |  |  | 3 | 6
Initial Circuit Breaker configuration
| Circuit Breakers |  |  |  |  | Post Blackout |  | Pre-restoration status required |  | Restoration Option 1
Substations | Name | Busbar Name | Busbar Number | CB Number | kV | CB status | Comments | Pre-restoration status required | Comments | CB status | Stage | Step | Seq | Comments
Chapelcross | Grid 1 | CHAPA3A1 | 698 | tbc | 33 | CLOSED |  | OPEN | via existing SCADA control | OPEN |  |  | -
Chapelcross | Grid 2 | CHAPA3A2 | 698 | tbc | 33 | CLOSED |  | OPEN | via existing SCADA control | OPEN |  |  | -
Chapelcross | Annan No.1 | CHAPA3A1 | 698 | 13 | 33 | OPEN | UF trip | OPEN | may want to SCADA open in case not opened | CLOSED | 3 | 1 | 3-1 | Annan No.1 33kV, all 11kV
Chapelcross | Lockerbie No.1 | CHAPA3A1 | 698 | 14 | 33 | OPEN | UF trip | OPEN | may want to SCADA open in case not opened | CLOSED | 3 | 5 | 3-5 | Lockerbie No.1 Dumfries?
Chapelcross | Middlebie SWS | CHAPA3A1 | 698 | 12 | 33 | CLOSED |  | CLOSED |  | CLOSED | 2 | 3 | 2-3 | Chapelcross to Ewe Hill WF via MIBI3
Chapelcross | Gretna No.2 | CHAPA3A1 | 698 | 11 | 33 | CLOSED |  | OPEN | via existing SCADA control |  | 3 | 4 | 3-4 | Gretna No.2
Chapelcross | Bus section |  | 698 | 01 | 33 | CLOSED |  | CLOSED | tbc by SCADA | CLOSED |  |  | -
Chapelcross | Langholm No.2/Newcastleton | CHAPA3A2 | 698 | 21 | 33 | CLOSED |  | OPEN | via existing SCADA control | CLOSED | 3 | 3 | 3-3 | Gretna No.1/Lang No.2/Newcastleton
Chapelcross | Lockerbie No.2 | CHAPA3A2 | 698 | 22 | 33 | OPEN | UF trip | OPEN | may want to SCADA open in case not opened |  |  |  | -
Chapelcross | Annan No.2 | CHAPA3A2 | 698 | 23 | 33 | OPEN | UF trip | OPEN | may want to SCADA open in case not opened | CLOSED | 3 | 2 | 3-2 | Annan No.2 33kV, all 11kV
Chapelcross | Steven's Croft | CHAPA3A1 | 698 | 15 | 33 | CLOSED |  | CLOSED |  | CLOSED | 2 | 1 | 2-1 | Energise Minsca WF
Chapelcross | Minsca WF | CHAPA3A2 | 698 | 24 | 33 | CLOSED |  | CLOSED |  | CLOSED | 2 | 1 | 2-1 | Energise Minsca WF
..
Stevens Croft SPD S/S | Chapelcross | STCR3- | 699 | 10 | 33 | CLOSED |  | OPEN | via existing SCADA control | CLOSED |  |  | -
Stevens Croft SPD S/S | Steven's Croft | STCR3- | 699 | 11 | 33 | OPEN | via G59 | CLOSED |  | CLOSED | 1 | 2 | 1-2 | Energise Steven's Croft
Stevens Croft Customer S/S | Step-up transformer | tbc | tbc | tbc | 33 | OPEN | i/t from SPD G59, tbc | OPEN | Customer's equipment | CLOSED | 1 | 1 | 1-1 | Energise Steven's Croft
..
Annan 33/11kV | Annan No.2 | ANAN5- | 662 | 20 | 11 | CLOSED |  | OPEN | via existing SCADA control |  |  |  | -
Annan 33/11kV | All other 11kV CBs | ANAN5- | 662 |  | 11 | CLOSED |  | CLOSED | Network 11kV G59 connections will be open |  |  |  | -
Annan 33/11kV | Annan No.1 | ANAN5- | 662 | 10 | 11 | CLOSED |  | CLOSED
..
Lockerbie 33/11kV | Lockerbie No.1 | LOBI3A | 694 | 12 | 33 | CLOSED |  | CLOSED |  | CLOSED |  |  | -
Lockerbie 33/11kV | Kirkbank/Moffat No.1 | LOBI3A | 694 | 13 | 33 | CLOSED |  | OPEN | via existing SCADA control | CLOSED | 3 | 6 | 3-6 | Kbank/Moffat No.1
Lockerbie 33/11kV | Lockerbie No.2 | LOBI3B | 694 | 22 | 33 | CLOSED |  | CLOSED |  | CLOSED |  |  | -
Lockerbie 33/11kV | Moffat No.2 | LOBI3B | 694 | 23 | 33 | CLOSED |  | CLOSED |  | CLOSED |  |  | -
Lockerbie 33/11kV | Bus section |  | 694 | 01 | 33 | OPEN |  | OPEN | normally open | OPEN |  |  | -
Lockerbie 33/11kV | Lockerbie No.2 | LOBI5- | 679 | 20 | 11 | CLOSED |  | OPEN | via existing SCADA control |  |  |  | -
Lockerbie 33/11kV | All other 11kV CBs | LOBI5- | 679 |  | 1 | CLOSED |  | CLOSED | Network 11kV G59 connections will be open | CLOSED |  |  | -
Lockerbie 33/11kV | Lockerbie No.1 | LOBI5- | 679 | 10 | 11 | CLOSED |  | CLOSED
..
Kirkbank 33/11kV | All 11kV CBs | KIBA5- | 675 |  | 11 | CLOSED |  | CLOSED | Network 11kV G59 connections will be open | CLOSED |  |  | -
Kirkbank 33/11kV | Kirkbank No.1 |  |  | 10 | 11 | CLOSED |  | CLOSED
..
Moffat 33/11kV | Moffat No.2 | MOFT5- | 683 | 20 | 11 | CLOSED |  | OPEN | via existing SCADA control |  |  |  | -
Moffat 33/11kV | All 11kV CBs | MOFT5- | 683 |  | 11 | CLOSED |  | CLOSED | Network 11kV G59 connections will be open |  |  |  | -
Moffat 33/11kV | Moffat No.1 |  |  | 10 |  | CLOSED |  | CLOSED
..
Middlebie 33kV Sw Stn | Chapelcross | MIBI3- | 780 | 12 | 33 | CLOSED |  | CLOSED |  | CLOSED |  |  | -
Middlebie 33kV Sw Stn | Ewe Hill WF | MIBI3- | 780 | 13 | 33 | CLOSED |  | CLOSED |  | CLOSED |  |  | -
Middlebie 33kV Sw Stn | Langholm No.1 | MIBI3- | 780 | 14 | 33 | CLOSED |  | OPEN | via existing SCADA control | CLOSED | 3 | 3 | 3-3 | Langholm No.1 33kV
Middlebie 33kV Sw Stn | Middlebie 33/11 | MIBI3- | 780 | 11 | 33 | CLOSED |  | OPEN | via existing SCADA control |  |  |  | -
Middlebie 33/11kV | All 11kV CBs | MIBI5- | 682 |  | 11 | CLOSED |  | CLOSED | Network 11kV G59 connections will be open | CLOSED |  |  | -
Middlebie 33/11kV | Middlebie No.1 |  |  | 10 | 10 | CLOSED |  | CLOSED
..
Ewe Hill WF SPD S/S | Middlebie | EWHC3- | 781 | 12 | 33 | CLOSED |  | CLOSED |  | CLOSED |  |  | -
Ewe Hill WF SPD S/S | Ewe Hill WF | EWHC3- | 781 | 11 | 33 | OPEN | via G59 | OPEN |  | CLOSED | 2 | 5 | 2-5 | Energise Ewe Hill WF, load only, MW only when instructed
Ewe Hill WF Customer S/S | SPD substation | tbc | tbc | tbc | 33 | OPEN | i/t from SPD G59, tbc | OPEN | Customer's equipment | CLOSED | 2 | 4 | 2-4 | Energise Ewe Hill WF, load only, MW only when instructed
Ewe Hill WF Customer S/S | All 33 kV feeders | tbc | tbc | tbc | 33 | OPEN | i/t from SPD G59, tbc | OPEN | Customer's equipment | CLOSED | 2 | 4 | 2-4 | Energise Ewe Hill WF, load only, MW only when instructed
..
Langholm 33/11kV | Bus section |  | 692 | 01 | 33 | OPEN |  | OPEN | normally open | OPEN |  |  | -
Langholm 33/11kV | Langholm No.2 | LAHO5- | 676 | 20 | 11 | CLOSED |  | OPEN | via existing SCADA control |  |  |  | -
Langholm 33/11kV | All other 11kV CBs | LAHO5- | 676 |  | 11 | CLOSED |  | CLOSED | Direct & network 11kV G59 will be open | CLOSED |  |  | -
Langholm 33/11kV | Langholm No.1 |  |  | 10 |  | CLOSED |  | CLOSED
..
Newcastleton 33/11kV | All 11kV CBs | NEWC5- | 123 |  | 11 | CLOSED |  | CLOSED | Direct & network 11kV G59 will be open | CLOSED |  |  | -
Newcastleton 33/11kV | Newcastleton No.1 |  |  | 10 |  | CLOSED |  | CLOSED
..
Gretna 33/11kV | Bus section |  | 691 | 01 | 33 | OPEN |  | OPEN | normally open | OPEN |  |  | -
Gretna 33/11kV | Grid 1 | GRNA5- | 673 | 10 | 11 | CLOSED |  | OPEN | via existing SCADA control |  |  |  | -
Gretna 33/11kV | All other 11kV CBs | GRNA5- | 673 |  | 11 | CLOSED |  | CLOSED | Direct & network 11kV G59 will be open | CLOSED |  |  | -
OPEN
Gretna 33/11kV | Gretna No.2 |  |  | 20 | 11 |  |  | CLOSED
..
Minsca WF SPD S/S | Chapelcross | MINS3- | 761 | tbc | 33 | CLOSED |  | CLOSED |  | CLOSED |  |  | -
Minsca WF SPD S/S | Minsca WF | MINS3- | 761 | tbc | 33 | OPEN | via G59 | OPEN |  | CLOSED | 2 | 2 | 2-2 | Energise Minsca WF, load only, MW only when instructed
Minsca WF Customer S/S | SPD substation | tbc | tbc | tbc | 33 | OPEN | i/t from SPD G59, tbc | OPEN | Customer's equipment | CLOSED | 2 | 3 | 2-3 | Energise Minsca WF, load only, MW only when instructed
Minsca WF Customer S/S | All 33 kV feeders | tbc | tbc | tbc | 33 | OPEN | i/t from SPD G59, tbc | OPEN | Customer's equipment | CLOSED | 2 | 3 | 2-3 | Energise Minsca WF, load only, MW only when instructed
..
Note on I8: Dieter Gutschow: Will change colour automatically if different from post blackout
Note on I28: Lauren McVey: Should this be closed? As open on diagram and not previously listed. IT is open in scenraio 1
Note on I37: Lauren McVey: Should this be closed? As open on diagram and not previously listed. IT is open in scenraio 1
Note on I40: Lauren McVey: Should this be closed? As open on diagram and not previously listed. IT is open in scenraio 1
Note on I44: Lauren McVey: Should this be closed? As open on diagram and not previously listed. IT is open in scenraio 1
Note on I51: Lauren McVey: Should this be closed? As open on diagram and not previously listed. IT is open in scenraio 1
Note on I61: Lauren McVey: Should this be closed? As open on diagram and not previously listed. IT is open in scenraio 1
Note on I64: Lauren McVey: Should this be closed? As open on diagram and not previously listed. IT is open in scenraio 1
Note on I70: Lauren McVey: Should this be closed? As open on diagram and not previously listed. IT is open in scenraio 1

## CB Config Option 2
Initial Circuit Breaker Configuration - Restoration Option 2: Simultaneous restoration of Steven's Croft generator, Chapel Cross Busbars and Wind Farms | [13 empty] | Brkr Status
Description: | [13 empty] | OPEN
Simultaneous restoration of Steven's Croft generator, Chapel Cross Busbars and Wind Farms. Followed by sequential restoration of demand as per Options 1.
Initial Circuit Breaker configuration
| Circuit Breakers |  |  |  |  | Post Blackout |  | Pre-restoration status required
Substations | Name | Busbar Name | Busbar Number | CB Number | kV | CB status | Comments | Scenario A | Scenario B | Scenario C | Scenario D | Scenario E | Scenario F
[8 empty] | Energise only one 33/11kV trfr - full load | Energise both 33/11kV trfrs - full load | Energise trfr1 - half load, then energise trfr 2 - rest of load | Energise only one trfr - then switch full load | Energise trfr1 - then switch half load, then energise trfr 2 - and switch rest of load | Energise one trfr, switch 11kV load sequentially
Chapelcross Grid 33kV Busbar | Grid 1 | CHAPA3A1 | 698 | tbc | 33 | CLOSED |  | OPEN
| Grid 2 | CHAPA3A2 | 698 | tbc | 33 | CLOSED |  | OPEN
| Annan No.1 | CHAPA3A1 | 698 | 14 | 33 | OPEN | UF trip | OPEN
| Lockerbie No.1 | CHAPA3A1 | 698 | 13 | 33 | OPEN | UF trip | OPEN
| Middlebie SWS | CHAPA3A1 | 698 | 12 | 33 | CLOSED |  | CLOSED
| Gretna No.2 | CHAPA3A1 | 698 | 11 | 33 | CLOSED |  | OPEN
| Bus section |  | 698 | 01 | 33 | CLOSED |  | CLOSED
| Langholm No.2/Newcastleton | CHAPA3A2 | 698 | 21 | 33 | CLOSED |  | OPEN
| Lockerbie No.2 | CHAPA3A2 | 698 | 22 | 33 | OPEN | UF trip | OPEN
| Annan No.2 | CHAPA3A2 | 698 | 23 | 33 | OPEN | UF trip | OPEN
| Steven's Croft | CHAPA3A1 | 698 | 15 | 33 | CLOSED |  | CLOSED
| Minsca WF | CHAPA3A2 | 698 | 24 | 33 | CLOSED |  | CLOSED
Steven's Croft SPD S/S | Chapelcross | STCR3- | 699 | 10 | 33 | CLOSED |  | OPEN
| Steven's Croft | STCR3- | 699 | 11 | 33 | OPEN | via G59 | CLOSED
Steven's Croft Customer S/S | Step-up transformer | tbc | tbc | tbc | 33 | OPEN | i/t from SPD G59, tbc | OPEN
Annan Primary Substation 33/11kV | Annan T1 | ANAN5- | 662 | 10 | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | OPEN | OPEN | OPEN
| Annan T2 | ANAN5- | 662 | 20 | 11 | CLOSED |  | OPEN | CLOSED | CLOSED | OPEN | OPEN | OPEN
| Bus section | ANAN5- | 662 | 01 | 11 | CLOSED |  | CLOSED | CLOSED | OPEN | CLOSED | OPEN | CLOSED
| All other 11kV CBs | ANAN5- | 662 | 01 | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | OPEN
Lockerbie Switching Station 33kV | Lockerbie No.1 | LOBI3A | 694 | 12 | 33 | CLOSED |  | CLOSED
| Kirkbank/Moffat No.1 | LOBI3A | 694 | 13 | 33 | CLOSED |  | OPEN
| Lockerbie No.2 | LOBI3B | 694 | 22 | 33 | CLOSED |  | CLOSED
| Moffat No.2 | LOBI3B | 694 | 23 | 33 | CLOSED |  | OPEN
| Bus section | LOBI3- | 694 | 01 | 33 | OPEN |  | OPEN
Lockerbie Primary Substation 33/11kV | Lockerbie T1 | LOBI5- | 679 | 10 | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | OPEN | OPEN | OPEN
| Lockerbie T2 | LOBI5- | 679 | 20 | 11 | CLOSED |  | OPEN | CLOSED | CLOSED | OPEN | OPEN | OPEN
| Bus section | LOBI5- | 679 | 01 | 11 | CLOSED |  | CLOSED | CLOSED | OPEN | CLOSED | OPEN | CLOSED
| All other 11kV CBs | LOBI5- | 679 | 01 | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | OPEN
Kirkbank 33/11kV | All 11kV CBs | KIBA5- | 675 |  | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | OPEN | OPEN | OPEN
Moffat Primary Substation 33/11kV | Moffat T1 | MOFT5- | 683 | 10 | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | OPEN | OPEN | OPEN
| Moffat T2 | MOFT5- | 683 | 20 | 11 | CLOSED |  | OPEN | CLOSED | CLOSED | OPEN | OPEN | OPEN
| Bus section | MOFT5- | 683 | 01 | 11 | CLOSED |  | CLOSED | CLOSED | OPEN | CLOSED | OPEN | CLOSED
| All 11kV CBs | MOFT5- | 683 |  | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | OPEN
Middlebie 33kV Switching Station | Chapelcross | MIBI3- | 780 | 12 | 33 | CLOSED |  | CLOSED
| Ewe Hill WF | MIBI3- | 780 | 13 | 33 | CLOSED |  | CLOSED
| Langholm No.1 | MIBI3- | 780 | 14 | 33 | CLOSED |  | OPEN
| Middlebie 33/11 | MIBI3- | 780 | 11 | 33 | CLOSED |  | OPEN
Middlebie Primary Substation 33/11kV | Middlebie T1 | MIBI3- | 780 | 10 | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | OPEN | OPEN | OPEN
| All 11kV CBs | MIBI5- | 682 |  | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | OPEN
Ewe Hill WF SPD S/S | Middlebie | EWHC3- | 781 | 12 | 33 | CLOSED |  | CLOSED
| Ewe Hill WF | EWHC3- | 781 | 11 | 33 | OPEN | via G59 | OPEN
Ewe Hill WF Customer S/S | SPD substation | tbc | tbc | tbc | 33 | OPEN | i/t from SPD G59, tbc | OPEN
Langholm 33kV | Bus section |  | 692 | 01 | 33 | OPEN |  | OPEN
Langholm Primary Substation 33/11kV | T1 | LAHO5- | 676 | 10 | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | OPEN | OPEN | OPEN
| T2 | LAHO5- | 676 | 20 | 11 | CLOSED |  | OPEN | CLOSED | CLOSED | OPEN | OPEN | OPEN
| Bus section | LAHO5- | 676 | 01 | 11 | CLOSED |  | CLOSED | CLOSED | OPEN | CLOSED | OPEN | CLOSED
| All other 11kV CBs | LAHO5- | 676 |  | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | OPEN
Newcastleton Primary Substation 33/11kV | T1 | NEWC5- | 123 |  | 10 | CLOSED |  | CLOSED | CLOSED | CLOSED | OPEN | OPEN | OPEN
| All 11kV CBs | NEWC5- | 123 |  | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | OPEN
Gretna 33kV | Bus section |  | 691 | 01 | 33 | OPEN |  | OPEN
Gretna Primary Substation 33/11kV | T1 | GRNA5- | 673 | 10 | 11 | CLOSED |  | OPEN | CLOSED | CLOSED | OPEN | OPEN | OPEN
| T2 | GRNA5- | 673 | 20 | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | OPEN | OPEN | OPEN
| Bus section | GRNA5- | 673 | 01 | 11 | CLOSED |  | CLOSED | CLOSED | OPEN | CLOSED | OPEN | CLOSED
| All other 11kV CBs | GRNA5- | 673 |  | 11 | CLOSED |  | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | OPEN
Minsca WF SPD S/S | Chapelcross | MINS3- | 761 | tbc | 33 | CLOSED |  | CLOSED
| Minsca WF | MINS3- | 761 | tbc | 33 | OPEN | via G59 | OPEN
Minsca WF Customer S/S | SPD substation | tbc | tbc | tbc | 33 | OPEN | i/t from SPD G59, tbc | OPEN

## Restore Option 2
Restoration switching (Option 2): Simultaneous restoration of Steven's Croft generator, Chapel Cross Busbars and Wind Farms | [18 empty] | Brkr Status
Description: | [18 empty] | OPEN
Simultaneous restoration of Steven's Croft generator, Chapel Cross Busbars and Wind Farms. Followed by sequential restoration of demand as per Options 1. | [18 empty] | CLOSE
Restoration Actions
Stage |  | Step | Substation Name | Circuit Breaker Operation | [6 empty] | Circuit Energised |  |  | Transformers Energised |  | Block Loads |  |  |  |  | System studies results (OK vs Fail)
| Transformer energisation scenario |  |  | Busbar Name | Busbar Number | kV | Circuit | CB Number | CB action | Comment | Description | MVA | Cumulative MVA | Name (Substation, Trfr no) | MVA | Name | Max MVA | Min MVA | PF | Maximum % of DER | Load Flow Check | Voltage & Control check | Frequency response check | Transient stability check | System studies results check
0 |  |  | Steven's Croft generator has energised up to SPD Steven's Croft 33kV interface CB | [6 empty] | Start anchor DER
1 |  | 1 | Connecting Steven's Croft anchor generator to Chapelcross GSP, Minsca and Ewe Hill Wind farms
|  | 1.1 | Steven's Croft Cust S/S |  |  | 33 | Steven's Croft SPD s/s |  | CLOSE | Cust switching. Energise SPD 33 kV busbar and earthing Tx + Load bank | STCR3- - CHAPA3A1 |  |  |  | tbc
|  | 1.2 | Steven's Croft SPD S/S | STCR3- | 699 | 33 | Chapelcross | tbc | CLOSE | Energise 33kV cable to Chapelcross, BB, Minsca & Ewe Hill WF ccts.
2 |  | 2 | Restoration of Power Supply to Minsca Wind farm
|  | 2.1 | Minsca Customer S/S | tbc | tbc | 33 | 33 kV feeders | tbc | CLOSE | Energise cable feeders. Restore aux to WTGs. |  |  |  | Auxiliary transformer
No MWs from WTGs until instructed. Need to switch WTGs from voltage control mode to power factor control mode
3 |  | 3 | Restoration of Power Supply to Ewe Hill Wind farm
|  | 3.1 | EWE Hill Customer S/S | tbc | tbc | 33 | 33 kV feeders | tbc | CLOSE | Energise cable feeders. Restore aux to WTGs. |  |  |  | Auxiliary transformer | tbc | Ewe Hill WF Aux
No MWs from WTGs until instructed. Need to switch WTGs from voltage control mode to power factor control mode
Load restoration ss per Option 1.
4 |  | 4 | Restoration of Power Supply to Annan Primary Substation. Primary restoration options A-F considered.
| A | 4.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1 and pick up block load | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12 | Annan PS | 12.12
| B | 4.1 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T2 | 20 | CLOSE | Ensure CB 20 to be closed in pre-restoration
| B | 4.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformers T1 &T2 and pick up block load | CHAPA3A1 - ANANT1 CHAPA3A2 - ANNAT2 |  |  | Annan T1 33/11kV Annan T2 33/11kV | 12 12 | Annan PS | 12.12
| B | 4.3 | Chapelcross | CHAPA3A2 | 698 | 33 | Annan No.2 | 23 | CLOSE | Restores No.2 33kV cct for security/protection purposes.
| C | 4.1 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T2 | 20 | CLOSE | Ensure CB 20 closed in pre-restoration
| C | 4.2 | Annan PS | ANAN5- | 662 | 11 | Bus section | 01 | OPEN | Run 2x11 kV sections (only viable if no closed 11kV rings)
| C | 4.3 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer T1 and pick up half block load | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12 | Annan PS | 6.06 tbc
| C | 4.4 | Chapelcross | CHAPA3A2 | 698 | 33 | Annan No.2 | 23 | CLOSE | Energise feeder transformer T2 and pick up half block load | CHAPA3A2 - ANANT2 |  |  | Annan T2 33/11kV | 12 | Annan PS | 6.06 tbc
| D | 4.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1 | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12
| D | 4.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Full load at Annan Primary | [5 empty] | Annan PS | 12.12
| E | 4.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1 | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12
| E | 4.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Half load at Annan Primary | [5 empty] | Annan PS | 6.06 tbc
| E | 4.3 | Annan PS | ANAN5- | 662 | 11 | 11kV bus-section | 01 | CLOSE | Close bus-section and energise second half of the Primary load | [5 empty] | Annan PS | 6.06 tbc
| F | 4.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1 | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12
| F | 4.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T1 | 10 | CLOSE | Energise 11kV busbar
| F | 4.3 | Annan PS | ANAN5- | 662 | 11 | 11kV feeders | tbc | CLOSE | Take on feeders one at a time | [5 empty] | Annan PS | ?
5 | A | 5 | Restoration of Power Supply to Middlebie PS
|  | 5.1 | Middlebie SWS | MIBI3- | 780 | 33 | Middlebie No.1 | 11 | CLOSE | Energise feeder transformer and pick up block load |  |  |  | Middlebie 33/11kV | 10 | Middlebie PS | 5.24
6 | A | 6 | Restoration of Power Supply to Langholm PS
|  | 6.1 | [7 empty] | Instruct Minsca WF (43 MVA) to generate 15MW.
|  | 6.2 | Middlebie SWS | MIBI3- | 780 | 33 | Langholm No.1 | 14 | CLOSE | Energise feeder transformer for T1 and pick up block load | MIBI3- - LAHO3A |  |  | Langholm T1 33/11kV | 12 | Langholm PS | 6.35
7 | A | 7 | Restoration of Power Supply to Gretna PS
|  | 7.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Gretna No.2 | 11 | CLOSE | Energise feeder transformer for T2 and pick up block load | CHAPA3A1 - GRNA3B |  |  | Gretna T2 33/11kV | 12 | Gretna PS | 7.1
8 | A | 8 | Restoration of Power Supply to Newcastelton PS
|  | 8.1 | Chapelcross | CHAPA3A2 | 698 | 33 | Gretna No.1, Langholm No.2, and Newcastelton. | 21 | CLOSE | Energise Newcastleton T1 and pick up block load | CHAPA3A2 - X3 X3 - GRNA3A X3 - LAHO3B |  |  | Newcastelton 33/11kV Gretna T1 33/11kV Langholm T2 33/11kV | 5 in LTDS 12 12 | Newcastelton PS | 1.09
9 | C | 9 | Restoration of Power Supply to Lockerbie PS Load 1 & 2
|  | 9.1 | [7 empty] | Instruct Minsca WF (43 MVA) to increase generation to 20MW.
|  | 9.2 | [7 empty] | Instruct Ewe WF (12.63 MVA) to generate 5 MW
|  | 9.3 | Lockerbie | LOBI3- | 679 | 33 | 11 kV bus section | 01 | OPEN | Run 2 x 11kV sections (only viable if no closed rings) [Bus section be OPEN already]
|  | 9.4 | Chapelcross | CHAPA3A1 | 698 | 33 | Lockerbie No.1 | 14 | CLOSE | Energise Lockerbie T1 & Lockerbie Load 1. Pick up half block load. | CHAPA3A1 - X1 X1 - LOBI3A |  |  | Lockerbie T1 33/11kV | 24 | Lockerbie PS | =14.65 / 2
|  | 9.5 | Chapelcross | CHAPA3A2 | 698 | 33 | Lockerbie No. 2 | 22 | CLOSE | Energise Lockerbie T2 & Lockerbie Load 2. Pick uo half block load. |  |  |  | Lockerbie T1 33/11kV | 24 | Lockerbie PS | =14.65 / 2
10 | C | 10 | Restoration of Power Supply to Kirkbank/Moffat PS Load 1
|  | 10.1 | Moffat | MOFT5- | 683 | 11 | 11kV bus section | 01 | OPEN | Run 2 x 11kV sections (only viable if no closed rings) [Bus section be OPEN already]
|  | 10.2 | Lockerbie | LOBI3A | 694 | 33 | Kirkbank & Moffat No.1 | 13 | CLOSE | Energise Moffat T1 and Load 1 and pick up block load. Delay before step 12 | LOBI3A - X4 X4 - KIBAT1 X4 - MOFTT1 |  |  | Kirkbank 33/11kV Moffat T1 33/11kV | 5 7.5 | Kirkbank PS Moffat T1 | 1.37
11 |  | 11 | Restoration of Power Supply to Moffat PS Load 2
|  | 11.1 | Lockerbie | LOBI3A | 694 | 33 | Moffat No. 2 | 23 | CLOSE | After cold load delay, energise Moffat T2 and Load 2 and pick up block load. |  |  |  | Moffat T2 33/11kV | 7.5 | Moffat T2
LOBI3A - X4 X4 - KIBAT1 X4 - MOFTT1
12 |  | 12 | Restore network to normal operating mode to improve supply security
|  | 12.1 | Annan PS | ANAN5- | 662 | 11 | 11kV bus section | 01 | CLOSE | Close bus section to improve supply security
|  | 12.2 | Lockerbie PS | LOBI3- | 679 | 11 | 11kV bus section | 01 | CLOSE | Close bus section to improve supply security
|  | 12.3 | Moffat PS | MOFT5- | 683 | 11 | 11kV bus section | 01 | CLOSE | Close bus section to improve supply security
|  | 12.4 | Langholm | LAHO5- | 676 | 11 | Langholm T2 | 20 | CLOSE | Connect T2 to improve supply security
|  | 12.5 | Gretna | GRNA5- | 673 | 11 | Gretna T1 | 10 | CLOSE | Connect T1 to improve supply security
Note on B31: Dieter Gutschow: Option C is preferred over option A due to overloading of transformers due to cold load pickup

## CB Config Option 3
Initial Circuit Breaker Configuration - Restoration Option 3 | [11 empty] | Brkr Status
Description: | [11 empty] | OPEN
Option 3A: Sequential 33kV Restoration and Chapelcross 132kV Grid 1 trfr incl Ecclefechan 132kV line and Grid 1 trfr Option 3B: Sequential 33kV Restoration and Chapelcross 132kV Grid 1 trfr excl Ecclefechan Option 3C: Simultaneous 33kV restoration and energisation of Chapelcross 132kV Grid 1 trfr incl Ecclefechan 132kV line and Grid trfr Option 3D : Simultaneous 33kV restoration and energisation on Chapelcross 132kV Grid 1 trfr excl Ecclefechan | [11 empty] | CLOSED
Option 3A and 3B builds on the CB configuration for option 1 plus the additional below Option 3C and 3D builds on the CB configuration for option 2 plus the additional below
Initial Circuit Breaker configuration
| Circuit Breakers |  |  |  |  | Post Blackout |  | Option 3A | Option 3B | Option 3C | Option 3D | Comments
Substations | Name | Busbar Name | Busbar Number | CB Number | kV | CB status | Comments | Pre-restoration status required | Pre-restoration status required | Pre-restoration status required | Pre-restoration status required
Chapelcross | Grid T1 | CHAP1-1 |  | Grid 1 | 33 | CLOSED |  | OPEN | OPEN | CLOSED | CLOSED
Chapelcross | Grid T2 | CHAP1-2 |  | Grid 2 | 33 | CLOSED |  | OPEN | OPEN | OPEN | OPEN
Chapelcross | Gretna No.1 | CHAP1-1 |  | 1105 | 132 | CLOSED |  | OPEN | OPEN | OPEN | OPEN
Chapelcross | Gretna No.2 | CHAP1-2 |  | 205 | 132 | CLOSED |  | OPEN | OPEN | OPEN | OPEN
Chapelcross | Chapelcross 132kV busbar 1 | CHAP1-1 |  | 710 | 132 | CLOSED |  | OPEN | OPEN | CLOSED | OPEN
Chapelcross | Dumfries No.2 | CHAP1-2 |  | 800 | 132 | CLOSED |  | OPEN | OPEN | OPEN | OPEN
Chapelcross | Chapelcross 132kV busbar 2 | CHAP1-2 |  | 410 | 132 | CLOSED |  | OPEN | OPEN | OPEN | OPEN
Chapelcross | Harker | CHAP1-2 |  | 1005 | 132 | CLOSED |  | OPEN | OPEN | OPEN | OPEN
Chapelcross | Dumfries No.1 | CHAP1-1 |  | 500 | 132 | CLOSED |  | OPEN | OPEN | OPEN | OPEN
Chapelcross | Bus Section | CHAP1- |  | 120 | 132 | CLOSED |  | OPEN | OPEN | OPEN | OPEN
Chapelcross | Ecclefechan No.1 | CHAP1-1 |  | 915 | 132 | CLOSED |  | CLOSED | OPEN | CLOSED | OPEN | Breaker 915 needs to be open for scenario where Ecclefechan No.1is excluded
Chapelcross | Ecclefechan No.2 | CHAP1-2 |  | 615 | 132 | OPEN |  | OPEN | OPEN | OPEN | OPEN | Breaker 615 should always be open to ensure Ecclefechan No.2 is not energised.
Ecclefechan | Railtrack |  |  | EC/S1 | 25 |  |  | OPEN | OPEN | OPEN | OPEN
Ecclefechan | Railtrack |  |  | EC/S2 | 25 |  |  | OPEN | OPEN | OPEN | OPEN
Note: The circuit breaker configuration is based on the planned GIS commissioning at Chapelcross in December 2020
Note on I8: Dieter Gutschow: Will change colour automatically if different from post blackout
Note on K8: Dieter Gutschow: Will change colour automatically if different from post blackout
Note on L8: Dieter Gutschow: Will change colour automatically if different from post blackout
Note on M8: Dieter Gutschow: Will change colour automatically if different from post blackout

## Restore Option 3A-D
Restoration switching - Option 3 | [18 empty] | Brkr Status
Description: | [18 empty] | OPEN
Option 3A: Sequential 33kV Restoration and Chapelcross 132kV Grid 1 trfr incl Ecclefechan 132kV line and Grid 1 trfr Option 3B: Sequential 33kV Restoration and Chapelcross 132kV Grid 1 trfr excl Ecclefechan Option 3C: Simultaneous 33kV restoration and energisation of Chapelcross 132kV Grid 1 trfr incl Ecclefechan 132kV line and Grid trfr Option 3D : Simultaneous 33kV restoration and energisation on Chapelcross 132kV Grid 1 trfr excl Ecclefechan | [18 empty] | CLOSE
Option 3A and 3B builds on the CB configuration for option 1 plus the additional below Option 3C and 3D builds on the CB configuration for option 2 plus the additional below
Stage 3A & B is the sequential energisation of the Chapelcross 132/33kV trf with and without the Ecclefechan No.1 circuit
Stage |  | Step | Substation Name | Circuit Breaker Operation | [6 empty] | Circuit Energised |  |  | Transformers Energised |  | Block Loads |  |  |  |  | System studies results (OK vs Fail)
| Transformer energisation scenario |  |  | Busbar Name | Busbar Number | kV | Circuit | CB Number | CB action | Comment | Description | MVA | Cumulative MVA | Name (Substation, Trfr no) | MVA | Name | Max MVA | Min MVA | PF | Maximum % of DER | Load Flow Check | Voltage & Control check | Frequency response check | Transient stability check | System studies results check
To energise Ecclefechan No 1.
Stages 1 and 2 are from Option 1 restoration
Chapelcross 33kV busbar energised as per option 1, with Grid 1 open
1 |  | 1.1 | Steven's Croft Cust S/S |  |  | 33 | Steven's Croft SPD s/s |  | CLOSE | Customer switching. Energise SPD 33 kV busbar and earthing trfr + Load bank
|  | 1.2 | Steven's Croft SPD S/S | STCR3- | 699 | 33 | Chapelcross | tbc | CLOSE | Energise 33kV cable to Chapelcross
2 |  | 2.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Steven's Croft 33 kV | 15 | CLOSE | Energise Chapelcross 33 kV busbars
3 |  | 3.1 | Chapelcross | Chapelcross 33kV | CHAP3A2 | 33 |  | Grid 1 | CLOSE | For Option 3B breaker 915 is OPEN to disconnect the Ecclefecan No.1 132kV single phase cct.
|  | 3.2 | Chapelcross | CHAP1 - 1 |  | 132 | Grid T1 to Busbar 1 | 710 | CLOSE | To connect Transformer 1 to Busbar 1
|  | 3.3 | Chapelcross | CHAP1 - 1 |  | 132 | Ecclefechan No.1 | 915 | CLOSE | For Option 3A to connect the Ecclefecan No.1 132kV cricuit.
Restore Load as per option 1
4 |  | 4 | Restoration of Power Supply to Minsca Wind farm
|  | 4.1 | Chapelcross | CHAPA3A2 | 698 | 33 | Minsca WF | 24 | CLOSE | Energise circuit and Minsca SPD 33 kV busbar | CHAPA3A2 - MINS3-
|  | 4.2 | Minsca SPD S/S | MINS3- | 761 | 33 | Customer S/S | tbc | CLOSE | Energise customer S/S 33 kV busbar
|  | 4.3 | Minsca Customer S/S | tbc | tbc | 33 | 33 kV feeders | tbc | CLOSE | Energise cable feeders. Restore aux to WTGs. |  |  |  | Auxiliary transformer
5 |  | 5 | Restoration of Power Supply to Ewe Hill Wind farm
|  | 5.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Middlebie SWS | 12 | CLOSE | Energise circuit to Ewe Hill WF via Middlebie SWS
|  | 5.2 | Ewe Hill SPD S/S | EWHC3- | 781 | 33 | Customer S/S | 11 | CLOSE | Energise customer S/S 33 kV busbar
|  | 5.3 | Ewe Hill Customer S/S | tbc | tbc | 33 | 33 kV feeders | tbc | CLOSE | Energise cable feeders. Restore aux to WTGs. |  |  |  | Auxiliary transformer | tbc | Ewe Hill WF Aux
No MWs from WTGs until instructed. Need to switch WTGs from voltage control mode to power factor control mode
Load restoration as per Option 1.
6 |  | 6 | Restoration of Power Supply to Annan Primary Substation using C
| A | 6.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1 and pick up block load | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12 | Annan PS | 12.12
| B | 6.1 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T2 | 20 | CLOSE | Ensure CB 20 to be closed in pre-restoration
| B | 6.2 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformers T1 &T2 and pick up block load | CHAPA3A1 - ANANT1 CHAPA3A2 - ANNAT2 |  |  | Annan T1 33/11kV Annan T2 33/11kV | 12 12 | Annan PS | 12.12
| B | 6.3 | Chapelcross | CHAPA3A2 | 698 | 33 | Annan No.2 | 23 | CLOSE | Restores No.2 33kV cct for security/protection purposes.
| C | 6.1 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T2 | 20 | CLOSE | Ensure CB 20 closed in pre-restoration
| C | 6.2 | Annan PS | ANAN5- | 662 | 11 | Bus section | 01 | OPEN | Run 2x11 kV sections (only viable if no closed 11kV rings)
| C | 6.3 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer T1 and pick up half block load | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12 | Annan PS | 6.06 tbc
| C | 6.4 | Chapelcross | CHAPA3A2 | 698 | 33 | Annan No.2 | 23 | CLOSE | Energise feeder transformer T2 and pick up half block load | CHAPA3A2 - ANANT2 |  |  | Annan T2 33/11kV | 12 | Annan PS | 6.06 tbc
| D | 6.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1 | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12
| D | 6.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Full load at Annan Primary | [5 empty] | Annan PS | 12.12
| E | 6.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1 | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12
| E | 6.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Half load at Annan Primary | [5 empty] | Annan PS | 6.06 tbc
| E | 6.3 | Annan PS | ANAN5- | 662 | 11 | 11kV bus-section | 01 | CLOSE | Close bus-section and energise second half of the Primary load | [5 empty] | Annan PS | 6.06 tbc
| F | 6.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1 | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12
| F | 6.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T1 | 10 | CLOSE | Energise 11kV busbar
| F | 6.3 | Annan PS | ANAN5- | 662 | 11 | 11kV feeders | tbc | CLOSE | Take on feeders one at a time | [5 empty] | Annan PS | ?
7 | A | 7 | Restoration of Power Supply to Middlebie PS
|  | 7.1 | Middlebie SWS | MIBI3- | 780 | 33 | Middlebie No.1 | 11 | CLOSE | Energise feeder transformer and pick up block load |  |  |  | Middlebie 33/11kV | 10 | Middlebie PS | 5.24
8 | A | 8 | Restoration of Power Supply to Langholm PS
|  | 8.1 | [7 empty] | Instruct Minsca WF (43 MVA) to generate 15MW.
|  | 8.2 | Middlebie SWS | MIBI3- | 780 | 33 | Langholm No.1 | 14 | CLOSE | Energise feeder transformer for T1 and pick up block load | MIBI3- - LAHO3A |  |  | Langholm T1 33/11kV | 12 | Langholm PS | 6.35
9 | A | 9 | Restoration of Power Supply to Gretna PS
|  | 9.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Gretna No.2 | 11 | CLOSE | Energise feeder transformer for T2 and pick up block load | CHAPA3A1 - GRNA3B |  |  | Gretna T2 33/11kV | 12 | Gretna PS | 7.1
10 | A | 10 | Restoration of Power Supply to Newcastelton PS
|  | 10.1 | Chapelcross | CHAPA3A2 | 698 | 33 | Gretna No.1, Langholm No.2, and Newcastelton. | 21 | CLOSE | Energise Newcastleton T1 and pick up block load | CHAPA3A2 - X3 X3 - GRNA3A X3 - LAHO3B |  |  | Newcastelton 33/11kV Gretna T1 33/11kV Langholm T2 33/11kV | 5 in LTDS 12 12 | Newcastelton PS | 1.09
11 | C | 11 | Restoration of Power Supply to Lockerbie PS Load 1 & 2
|  | 11.1 | [7 empty] | Instruct Minsca WF (43 MVA) to increase generation to 20MW.
|  | 11.2 | [7 empty] | Instruct Ewe WF (12.63 MVA) to generate 5 MW
|  | 11.3 | Lockerbie | LOBI3- | 679 | 33 | 11 kV bus section | 01 | OPEN | Run 2 x 11kV sections (only viable if no closed rings) [Bus section be OPEN already]
|  | 11.4 | Chapelcross | CHAPA3A1 | 698 | 33 | Lockerbie No.1 | 14 | CLOSE | Energise Lockerbie T1 & Lockerbie Load 1. Pick up half block load. | CHAPA3A1 - X1 X1 - LOBI3A |  |  | Lockerbie T1 33/11kV | 24 | Lockerbie PS | =14.65 / 2
|  | 11.5 | Chapelcross | CHAPA3A2 | 698 | 33 | Lockerbie No. 2 | 22 | CLOSE | Energise Lockerbie T2 & Lockerbie Load 2. Pick uo half block load. |  |  |  | Lockerbie T1 33/11kV | 24 | Lockerbie PS | =14.65 / 2
12 | C | 12 | Restoration of Power Supply to Kirkbank/Moffat PS Load 1
|  | 12.1 | Moffat | MOFT5- | 683 | 11 | 11kV bus section | 01 | OPEN | Run 2 x 11kV sections (only viable if no closed rings) [Bus section be OPEN already]
|  | 12.2 | Lockerbie | LOBI3A | 694 | 33 | Kirkbank & Moffat No.1 | 13 | CLOSE | Energise Moffat T1 and Load 1 and pick up block load. Delay before step 12 | LOBI3A - X4 X4 - KIBAT1 X4 - MOFTT1 |  |  | Kirkbank 33/11kV Moffat T1 33/11kV | 5 7.5 | Kirkbank PS Moffat T1 | 1.37
13 |  | 13 | Restoration of Power Supply to Moffat PS Load 2
|  | 13.1 | Lockerbie | LOBI3A | 694 | 33 | Moffat No. 2 | 23 | CLOSE | After cold load delay, energise Moffat T2 and Load 2 and pick up block load. |  |  |  | Moffat T2 33/11kV | 7.5 | Moffat T2
LOBI3A - X4 X4 - KIBAT1 X4 - MOFTT1
14 |  | 14 | Restore network to normal operating mode to improve supply security
|  | 14.1 | Annan PS | ANAN5- | 662 | 11 | 11kV bus section | 01 | CLOSE | Close bus section to improve supply security
|  | 14.2 | Lockerbie PS | LOBI3- | 679 | 11 | 11kV bus section | 01 | CLOSE | Close bus section to improve supply security
|  | 14.3 | Moffat PS | MOFT5- | 683 | 11 | 11kV bus section | 01 | CLOSE | Close bus section to improve supply security
|  | 14.4 | Langholm | LAHO5- | 676 | 11 | Langholm T2 | 20 | CLOSE | Connect T2 to improve supply security
|  | 14.5 | Gretna | GRNA5- | 673 | 11 | Gretna T1 | 10 | CLOSE | Connect T1 to improve supply security
Stage 3C & D is the simultaneous energisation of the Chapelcross 132/33kV trfr (as per option 2) with and without the Ecclefechan No.1 circuit
Stage |  | Step | Substation Name | Circuit Breaker Operation | [6 empty] | Circuit Energised |  |  | Transformers Energised |  | Block Loads |  |  |  |  | System studies results (OK vs Fail)
| Transformer energisation scenario |  |  | Busbar Name | Busbar Number | kV | Circuit | CB Number | CB action | Comment | Description | MVA | Cumulative MVA | Name (Substation, Trfr no) | MVA | Name | Max MVA | Min MVA | PF | Maximum % of DER | Load Flow Check | Voltage & Control check | Frequency response check | Transient stability check | System studies results check
To energise Ecclefechan No 1.
1 |  | 1.1 | Steven's Croft Cust S/S |  |  | 33 | Steven's Croft SPD s/s |  | CLOSE | Customer switching. .
|  | 1.2 | Chapelcross | CHAP1 - 1 |  | 132 | Ecclefechan No.1 | 915 | CLOSE | Energise SPD 33 kV busbar and earthing trfr + Load bank and Chapel Cross 132kV transformer.Energise Minsca & Ewe Hill WF ccts For option 3D breaker 915 is OPEN to prevent energisation of Ecclefechan No.1 132kV transformer. For Option 3C to connect the Ecclefecan No.1 132kV circuit.
CHAPA3A2 - MINS3-
Restore Load as per Option 2
2 |  | 2 | Restoration of Power Supply to Minsca Wind farm
|  | 2.1 | Minsca Customer S/S / PoC | tbc | tbc | 33 | 33 kV feeders | tbc | CLOSE | Energise cable feeders. Restore aux to WTGs.
No MWs from WTGs until instructed. Need to switch WTGs from voltage control mode to power factor control mode
3 |  | 3 | Restoration of Power Supply to Ewe Hill Wind farm
|  | 3.1 | EWE Hill Customer S/S / PoC | tbc | tbc | 33 | 33 kV feeders | tbc | CLOSE | Energise cable feeders. Restore aux to WTGs.
No MWs from WTGs until instructed. Need to switch WTGs from voltage control mode to power factor control mode
Load restoration as per Option 1.
4 |  | 4 | Restoration of Power Supply to Annan Primary Substation using C
| A | 4.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1 and pick up block load
| B | 4.1 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T2 | 20 | CLOSE | Ensure CB 20 to be closed in pre-restoration
| B | 4.2 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformers T1 &T2 and pick up block load
| B | 4.3 | Chapelcross | CHAPA3A2 | 698 | 33 | Annan No.2 | 23 | CLOSE | Restores No.2 33kV cct for security/protection purposes.
| C | 4.1 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T2 | 20 | CLOSE | Ensure CB 20 closed in pre-restoration
| C | 4.2 | Annan PS | ANAN5- | 662 | 11 | Bus section | 01 | OPEN | Run 2x11 kV sections (only viable if no closed 11kV rings)
| C | 4.3 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer T1 and pick up half block load
| C | 4.4 | Chapelcross | CHAPA3A2 | 698 | 33 | Annan No.2 | 23 | CLOSE | Energise feeder transformer T2 and pick up half block load
| D | 4.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1
| D | 4.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Full load at Annan Primary
| E | 4.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1
| E | 4.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Half load at Annan Primary
| E | 4.3 | Annan PS | ANAN5- | 662 | 11 | 11kV bus-section | 01 | CLOSE | Close bus-section and energise second half of the Primary load
| F | 4.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1
| F | 4.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T1 | 10 | CLOSE | Energise 11kV busbar
| F | 4.3 | Annan PS | ANAN5- | 662 | 11 | 11kV feeders | tbc | CLOSE | Take on feeders one at a time
5 | A | 5 | Restoration of Power Supply to Middlebie PS
|  | 5.1 | Middlebie SWS | MIBI3- | 780 | 33 | Middlebie No.1 | 11 | CLOSE | Energise feeder transformer and pick up block load
6 | A | 6 | Restoration of Power Supply to Langholm PS
|  | 6.1 | [7 empty] | Instruct Minsca WF (43 MVA) to generate 15MW.
|  | 6.2 | Middlebie SWS | MIBI3- | 780 | 33 | Langholm No.1 | 14 | CLOSE | Energise feeder transformer for T1 and pick up block load
7 | A | 7 | Restoration of Power Supply to Gretna PS
|  | 7.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Gretna No.2 | 11 | CLOSE | Energise feeder transformer for T2 and pick up block load
8 | A | 8 | Restoration of Power Supply to Newcastelton PS
|  | 8.1 | Chapelcross | CHAPA3A2 | 698 | 33 | Gretna No.1, Langholm No.2, and Newcastelton. | 21 | CLOSE | Energise Newcastleton T1 and pick up block load
9 | C | 9 | Restoration of Power Supply to Lockerbie PS Load 1 & 2
|  | 9.1 | [7 empty] | Instruct Minsca WF (43 MVA) to increase generation to 20MW.
|  | 9.2 | [7 empty] | Instruct Ewe WF (12.63 MVA) to generate 5 MW
|  | 9.3 | Lockerbie | LOBI3- | 679 | 33 | 11 kV bus section | 01 | OPEN | Run 2 x 11kV sections (only viable if no closed rings) [Bus section be OPEN already]
|  | 9.4 | Chapelcross | CHAPA3A1 | 698 | 33 | Lockerbie No.1 | 14 | CLOSE | Energise Lockerbie T1 & Lockerbie Load 1. Pick up half block load.
|  | 9.5 | Chapelcross | CHAPA3A2 | 698 | 33 | Lockerbie No. 2 | 22 | CLOSE | Energise Lockerbie T2 & Lockerbie Load 2. Pick up half block load.
10 | C | 10 | Restoration of Power Supply to Kirkbank/Moffat PS Load 1
|  | 10.1 | Moffat | MOFT5- | 683 | 11 | 11kV bus section | 01 | OPEN | Run 2 x 11kV sections (only viable if no closed rings) [Bus section be OPEN already]
|  | 10.2 | Lockerbie | LOBI3A | 694 | 33 | Kirkbank & Moffat No.1 | 13 | CLOSE | Energise Moffat T1 and Load 1 and pick up block load. Delay before step 12
11 |  | 11 | Restoration of Power Supply to Moffat PS Load 2
|  | 11.1 | Lockerbie | LOBI3A | 694 | 33 | Moffat No. 2 | 23 | CLOSE | After cold load delay, energise Moffat T2 and Load 2 and pick up block load.
12 |  | 12 | Restore network to normal operating mode to improve supply security
|  | 12.1 | Annan PS | ANAN5- | 662 | 11 | 11kV bus section | 01 | CLOSE | Close bus section to improve supply security
|  | 12.2 | Lockerbie PS | LOBI3- | 679 | 11 | 11kV bus section | 01 | CLOSE | Close bus section to improve supply security
|  | 12.3 | Moffat PS | MOFT5- | 683 | 11 | 11kV bus section | 01 | CLOSE | Close bus section to improve supply security
|  | 12.4 | Langholm | LAHO5- | 676 | 11 | Langholm T2 | 20 | CLOSE | Connect T2 to improve supply security
|  | 12.5 | Gretna | GRNA5- | 673 | 11 | Gretna T1 | 10 | CLOSE | Connect T1 to improve supply security
Note on B41: Dieter Gutschow: Option C is preferred over option A due to overloading of transformers due to cold load pickup
Note on B120: Dieter Gutschow: Option C is preferred over option A due to overloading of transformers due to cold load pickup

## CB Config Option 4
Initial Circuit Breaker Configuration - Restoration Option 4 & B: Sequential 33kV Restoration extending to Dumfries T1 / T2 | [9 empty] | Brkr Status
Description: | [9 empty] | OPEN
Option 4A - Sequential 33kV Restoration and Chapelcross 132kV Tx incl Dumfries T4 and 33kV busbar | [9 empty] | CLOSED
Option 4B - Sequential 33kV Restoration and Chapelcross 132kV Tx incl Dumfries T1 plus 33kV busbar
Initial Circuit Breaker configuration
| Circuit Breakers |  |  |  |  | Post Blackout |  | Option 4A | Option 4B
Substations | Name | Busbar Name | Busbar Number | CB Number | kV | CB status | Comments | Pre-restoration status required | Pre-restoration status required
Chapelcross | Grid T2 |  |  | Grid 2 | 33 | CLOSED |  | OPEN | OPEN
Chapelcross | Grid T1 |  |  | Grid 1 | 33 | CLOSED |  | OPEN | OPEN
Chapelcross | Bus Section | CHAP1 |  | 120 | 132 | CLOSED |  | OPEN | OPEN
Chapelcross | Gretna No.1 | CHAP1 - 1 |  | 1105 | 132 | CLOSED |  | OPEN | OPEN
Chapelcross | Gretna No.2 | CHAP1 - 2 |  | 205 | 132 | CLOSED |  | OPEN | OPEN
Chapelcross | Chapelcross 132kV busbar 1 | CHAP1 - 1 |  | 710 | 132 | CLOSED |  | OPEN | OPEN
Chapelcross | Dumfries No.2 | CHAP1 - 2 |  | 800 | 132 | CLOSED |  | OPEN | OPEN
Chapelcross | Chapelcross 132kV busbar 2 | CHAP1 - 2 |  | 410 | 132 | CLOSED |  | OPEN | OPEN
Chapelcross | Harker | CHAP1 - 2 |  | 1005 | 132 | CLOSED |  | OPEN | OPEN
Chapelcross | Dumfries No.1 | CHAP1 - 1 |  | 500 | 132 | CLOSED |  | OPEN | OPEN
Chapelcross | Ecclefechan No.1 | CHAP1 - 1 |  | 915 | 132 | CLOSED |  | OPEN | OPEN
Chapelcross | Ecclefechan No.2 | CHAP1 - 2 |  | 615 | 132 | CLOSED |  | OPEN | OPEN
Dumfries | Bus section | DUMF1 |  | 320 | 132 | CLOSED |  | OPEN | OPEN
Dumfries | Bus section | DUMF1 |  | 120 | 132 | CLOSED |  | OPEN | OPEN
IC1 Dumfries | Dumfries IC1 No.1 | IC1 |  | 31 | 33 | CLOSED |  | OPEN | OPEN
IC1 Dumfries | Dumfries IC1 No.2 | IC1 |  | 41 | 33 | CLOSED |  | OPEN | OPEN
Dumfries | Bus Section | DUMF3A1 |  | 653 02 | 33 | OPEN |  | OPEN | OPEN
Dumfries | Bus section | DUMF3A1 |  | 653 01 | 33 | CLOSED |  | CLOSED | CLOSED
Dumfries | Bus section | DUMF3I |  | 653 03 | 33 | OPEN |  | OPEN | OPEN
Dumfries | Bus section | DUMF3A2 |  | 653 22 | 33 | CLOSED |  | OPEN | OPEN
Dumfries | Grid 1B | DUMF3A1 |  | Grid 1B | 33 | CLOSED |  | OPEN | OPEN
Dumfries | Grid 1A | DUMF3A1 |  | Grid 1A | 33 | CLOSED |  | OPEN | OPEN
Dumfries | Grid 2A | DUMF3A2 |  | Grid 2A | 33 | CLOSED |  | OPEN | OPEN
Dumfries | Grid 2B | DUMF3A2 |  | Grid 2B | 33 | CLOSED |  | OPEN | OPEN
Dumfries | Grid 4 | DUMF3I |  | Grid 4 | 33 | CLOSED |  | OPEN | OPEN
Dumfries | 33kV bus section reactor | DUMF3A2 |  | 653 21 | 33 | CLOSED |  | OPEN | OPEN
Dumfries | 33kV bus section reactor | DUMF3A1 |  | 653 11 | 33 | CLOSED |  | OPEN | OPEN
Dumfries | Dalswinton 33kV Busbar | DUMF3A1 |  | 653 12 | 33 | CLOSED |  | OPEN | OPEN
Dumfries | Nothing connected | DUMF3A1 |  | 653 13 | 33 | CLOSED |  | OPEN | OPEN
Dumfries | Cargenbridge T1 | DUMF3A1 |  | 653 14 | 33 | CLOSED |  | OPEN | OPEN
Dumfries | Heathhall T1 | DUMF3A1 |  | 653 15 | 33 | CLOSED |  | OPEN | OPEN
Dumfries | Maxwelltown T1/ Stelrad Edingham T1 | DUMF3A1 |  | 653 16 | 33 | CLOSED |  | OPEN | OPEN
Dumfries | Lochside T2/ Dunscore T1/ Penpoint 33kV Busbar | DUMF3A1 |  | 653 17 | 33 | CLOSED |  | OPEN | OPEN
Dumfries | Nothing Connected | DUMF3A2 |  | 653 23 | 33 | CLOSED |  | OPEN | OPEN
Dumfries | Cargenbridge T2 | DUMF3A2 |  | 653 24 | 33 | CLOSED |  | OPEN | OPEN
Dumfries | Heathhall T2 | DUMF3A2 |  | 653 25 | 33 | CLOSED |  | OPEN | OPEN
Dumfries | Maxwelltown T2 | DUMF3A2 |  | 653 26 | 33 | CLOSED |  | OPEN | OPEN
Dumfries | Penpoint 33kV Busbar | DUMF3A2 |  | 653 27 | 33 | CLOSED |  | OPEN | OPEN
Dumfries | Carrutherstown 33kV | DUMF3A2 |  | 653 28 | 33 | CLOSED |  | OPEN | OPEN
Note: The circuit breaker configuration is based on the planned GIS commissioning at Chapelcross in December 2020
Need to ensure that 132kV isolators on Dumfries 1 and 2 are closed
Note on I8: Dieter Gutschow: Will change colour automatically if different from post blackout
Note on J8: Dieter Gutschow: Will change colour automatically if different from post blackout
Note on G35: Lauren McVey: check status of CB after blackout
Note on G36: Lauren McVey: check status of CB after blackout

## Restore Option 4A
Restoration switching - Option 4A: Sequential 33kV Restoration extending to Dumfries Grid T4 transformer | [17 empty] | Brkr Status
Description: | [17 empty] | OPEN
Expand from Chapelcross 132kV to Dumfries T4 | [17 empty] | CLOSE
Option 4A - Builds on option 1 with additional switching to Energise Dumfries 132kV T4
Restoration Actions
Stage | Step | Substation Name | Circuit Breaker Operation | [6 empty] | Circuit Energised |  |  | Transformers Energised |  | Block Loads |  |  |  |  | System studies results (OK vs Fail)
|  |  | Busbar Name | Busbar Number | kV | Circuit | CB Number | CB action | Comment | Description | MVA | Cumulative MVA | Name (Substation, Trfr no) | MVA | Name | Max MVA | Min MVA | PF | Maximum % of DER | Load Flow Check | Voltage & Control check | Frequency response check | Transient stability check | System studies results check
Stage 1 to 4 are the restoration steps from Option 1
1 | 1 | Steven's Croft generator has energised up to SPD Steven's Croft 33kV interface CB | [6 empty] | Start anchor DER
| 1 | Connecting Steven's Croft anchor generator to Chapelcross GSP
| 1.1 | Steven's Croft Cust S/S |  |  | 33 | Steven's Croft SPD s/s |  | CLOSE | Cust switching.Energise SPD 33 kV busbar and earthing trfr + Load bank | STCR3- - CHAPA3A1 |  |  |  | tbc
| 1.2 | Steven's Croft SPD S/S | STCR3- | 699 | 33 | Chapelcross | tbc | CLOSE | Energise 33kV cable to Chapelcross
2 | 2 | Energise Chapelcross 33kV Busbars
| 2.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Steven's Croft 33 kV | 15 | CLOSE | Energise Chapelcross 33 kV busbars
3 | 3 | Restoration of Power Supply to Minsca Windfarm
| 3.1 | Chapelcross | CHAPA3A2 | 698 | 33 | Minsca WF | 24 | CLOSE | Energise circuit and Minsca SPD 33 kV busbar | CHAPA3A2 - MINS3-
| 3.2 | Minsca SPD S/S | MINS3- | 761 | 33 | Customer S/S | tbc | CLOSE | Energise customer S/S 33 kV busbar
| 3.3 | Minsca Customer S/S | tbc | tbc | 33 | 33 kV feeders | tbc | CLOSE | Energise cable feeders. Restore aux supply to WTGs. |  |  |  | Auxiliary transformer
No MWs from WTGs until instructed. Option to switch WTGs from voltage control mode to power factor control mode
4 | 4 | Restoration of Power Supply to Ewe Hill Windfarm
| 4.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Middlebie SWS | 12 | CLOSE | Energise circuit to Ewe Hill WF via Middlebie SWS | CHAPA3A1 - MIBI3- MIBI3- - EWHC3-
| 4.2 | Ewe Hill SPD S/S | EWHC3- | 781 | 33 | Customer S/S | 11 | CLOSE | Energise customer S/S 33 kV busbar
| 4.3 | Ewe Hill Customer S/S | tbc | tbc | 33 | 33 kV feeders | tbc | CLOSE | Energise cable feeders. Restore aux to WTGs. |  |  |  | Auxiliary transformer | tbc | Ewe Hill WF Aux
No MWs from WTGs until instructed. Option to switch WTGs from voltage control mode to power factor control mode
Stages 5 and 6 are the additional switching required to Energise Dumfries No 1 132kV plus 33kV bus bar and bring on Dalswinton WF and Cargenbridge Primary
5 | 5.1 | Chapelcross | Chap3A2 |  | 33 | Chapelcross 132/33kV transformer 1 | Grid T1 | CLOSE | Close Chapelcross Grid T1 breaker to energise 132/33kV T1 transformer
| 5.2 | Chapelcross | CHAP1 |  | 132 | Chapelcross 132kV busbar | 710 | CLOSE | Close Chapelcross 132kV breaker 710 to energise 132kV Main Busbar 1
| 5.3 | Chapelcross | CHAP1 |  | 132 | Dumfries No.1 | 500 | CLOSE | Close Chapelcross 132kV breaker 500 to energise Dumfries Circuit 1
6 | 6.1 | Dumfries | DUMF3I |  | 33 | Dumfries ICI 33kV busbar | Grid 4 | CLOSE | Close Dumfries 132kV breaker Grid 4 to energise Dumfries ICI 33kV bus bar
| 6.2 | Dumfries | DUMF3I |  | 33 | Dumfries ICI 33kV busbar | 653 03 | CLOSE | Close breaker to Energise whole ICI 33kV bus bar
| 6.3 | Dumfries | DUMF3I |  | 33 | Dumfries ICI 33kV busbar | 653 02 | CLOSE | Close breakers to energise Dumfries 33kV main busbar no. 2 and main busbar no. 1
| 6.4 | Dumfries | DUMF3A2 |  | 33 | Dumfries 33kV busbar no. 2 | 653 22 | CLOSE
| 6.5 | Dumfries | DUMF3A1 |  | 33 | Dalswinton Wind Farm | 653 12 | CLOSE | Close Dumfries 33kV breaker to Dalswinton wind farm
| 6.6 | Dumfries | DUMF3A1 |  | 33 | Cargenbridge Primary No.1 | 653 14 | CLOSE | Close Dumfries 33kV breaker to energise Cargenbridge primary substation
Restore Load as per option 1 from stage 5 onwards
Note: The circuit breaker configuration is based on the planned GIS commissioning at Chapelcross in December 2020

## Restore Option 4B
Restoration switching - Option 4B: Sequential 33kV Restoration extending to Dumfries Grid T1B & T1A transfomer | [17 empty] | Brkr Status
Description: | [17 empty] | OPEN
Expand from Chapelcross 132kV to Dumfries T1B & T1A | [17 empty] | CLOSE
Option 4B - Builds on option 1 with additioanal switching to Energise Dumfries 132kV T1B plus 33kV bus bar
Restoration Actions
Stage | Step | Substation Name | Circuit Breaker Operation | [6 empty] | Circuit Energised |  |  | Transformers Energised |  | Block Loads |  |  |  |  | System studies results (OK vs Fail)
|  |  | Busbar Name | Busbar Number | kV | Circuit | CB Number | CB action | Comment | Description | MVA | Cumulative MVA | Name (Substation, Trfr no) | MVA | Name | Max MVA | Min MVA | PF | Maximum % of DER | Load Flow Check | Voltage & Control check | Frequency response check | Transient stability check | System studies results check
Stage 1 to 4 are the restoration steps from Option 1
1 | 1 | Steven's Croft generator has energised up to SPD Steven's Croft 33kV interface CB | [6 empty] | Start anchor DER
| 1 | Connecting Steven's Croft anchor generator to Chapelcross GSP
| 1.1 | Steven's Croft Cust S/S |  |  | 33 | Steven's Croft SPD s/s |  | CLOSE | Cust switching.Energise SPD 33 kV busbar and earthing trfr + Load bank | STCR3- - CHAPA3A1 |  |  |  | tbc
| 1.2 | Steven's Croft SPD S/S | STCR3- | 699 | 33 | Chapelcross | tbc | CLOSE | Energise 33kV cable to Chapelcross
2 | 2 | Energise Chapelcross 33kV Busbars
| 2.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Steven's Croft 33 kV | 15 | CLOSE | Energise Chapelcross 33 kV busbars
3 | 3 | Restoration of Power Supply to Minsca Windfarm
| 3.1 | Chapelcross | CHAPA3A2 | 698 | 33 | Minsca WF | 24 | CLOSE | Energise circuit and Minsca SPD 33 kV busbar | CHAPA3A2 - MINS3-
| 3.2 | Minsca SPD S/S | MINS3- | 761 | 33 | Customer S/S | tbc | CLOSE | Energise customer S/S 33 kV busbar
| 3.3 | Minsca Customer S/S | tbc | tbc | 33 | 33 kV feeders | tbc | CLOSE | Energise cable feeders. Restore aux supply to WTGs. |  |  |  | Auxiliary transformer
No MWs from WTGs until instructed. Option to switch WTGs from voltage control mode to power factor control mode
4 | 4 | Restoration of Power Supply to Ewe Hill Windfarm
| 4.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Middlebie SWS | 12 | CLOSE | Energise circuit to Ewe Hill WF via Middlebie SWS | CHAPA3A1 - MIBI3- MIBI3- - EWHC3-
| 4.2 | Ewe Hill SPD S/S | EWHC3- | 781 | 33 | Customer S/S | 11 | CLOSE | Energise customer S/S 33 kV busbar
| 4.3 | Ewe Hill Customer S/S | tbc | tbc | 33 | 33 kV feeders | tbc | CLOSE | Energise cable feeders. Restore aux to WTGs. |  |  |  | Auxiliary transformer | tbc | Ewe Hill WF Aux
No MWs from WTGs until instructed. Option to switch WTGs from voltage control mode to power factor control mode
Stages 5 and 6 are the additional switching required to Energise Dumfries 132kV 1A and 1B plus the 33kV busbar
5 | 5.1 | Chapelcross | Chap3A2 |  | 33 | Chapelcross 132/33kV transformer | Grid T1 | CLOSE | Close Chapelcross Grid T1 breaker to energise 132/33kV transformer T1
| 5.2 | Chapelcross | CHAP1 |  | 132 | Chapelcross 132kV busbar | 710 | CLOSE | Close Chapelcross 132kV breaker 710 to energise 132kV Busbar 1
| 5.3 | Chapelcross | CHAP1 |  | 132 | Chapelcross 132 busbar | 120 | CLOSE | Close bus section breaker to energise Busbar 2
| 5.4 | Chapelcross | CHAP1 |  | 132 | Dumfries No.2 | 800 | CLOSE | Close Chapelcross 132kV breaker 800 to energise Dumfries No.2
6 | 6.1 | Dumfries | DUMF3A1 |  | 33 | Dumfries 33kV busbar | Grid 1B | CLOSE | Close Dumfries 132kV breaker Grid 1B to energise Dumfries 33kV bus bar
| 6.2 | Dumfries | DUMF3A1 |  | 33 | Dalswinton Wind Farm | 653 12 | CLOSE | Close Dumfries 33kV breaker to Dalswinton wind farm
| 6.3 | Dumfries | DUMF3A1 |  | 33 | Cargenbridge Primary No.1 | 653 14 | CLOSE | Close Dumfries 33kV breaker to energise Cargenbridge primary substation
Restore Load as per option 1 from stage 5 onwards

## CB Config Option 5
Initial Circuit Breaker Configuration - Restoration Option 5: Sequential 33kV Restoration extending to Gretna 400kV | [9 empty] | Brkr Status
Description: | [9 empty] | OPEN
Sequential 33kV Restoration and Chapelcross 132kV Tx incl Gretna 400kV and Ewe Hill WF 132kV | [9 empty] | CLOSED
Initial Circuit Breaker configuration
| Circuit Breakers |  |  |  |  | Post Blackout |  | Pre-restoration status required
Substations | Name | Busbar Name | Busbar Number | CB Number | kV | CB status | Comments | Pre-restoration status required | Comments
Chapelcross | Grid T1 |  |  | Grid 1 | 33 | CLOSED |  | OPEN
Chapelcross | Grid T2 |  |  | Grid 2 | 33 | CLOSED |  | OPEN
Chapelcross | Bus Coupler | CHAP1 |  | 1530 | 132 | CLOSED |  | OPEN
Chapelcross | Gretna No.1 | CHAP1 - 1 |  | 1105 | 132 | CLOSED |  | OPEN
Chapelcross | Gretna No.2 | CHAP1 - 2 |  | 205 | 132 | CLOSED |  | OPEN
Chapelcross | Chapelcross 132kV busbar 1 | CHAP1 - 1 |  | 710 | 132 | CLOSED |  | OPEN
Chapelcross | Dumfries No.2 | CHAP1 - 1 |  | 800 | 132 | CLOSED |  | OPEN
Chapelcross | Chapelcross 132kV busbar 2 | CHAP1 - 2 |  | 410 | 132 | CLOSED |  | OPEN
Chapelcross | Harker | CHAP1 - 2 |  | 1005 | 132 | CLOSED |  | OPEN
Chapelcross | Dumfries No.1 | CHAP1 - 2 |  | 500 | 132 | CLOSED |  | OPEN
Chapelcross | Ecclefechan No.1 | CHAP1 -1 |  | 915 | 132 | CLOSED |  | OPEN
Gretna | 400kV substation | GRNA1 |  | 780 | 132 | CLOSED |  | OPEN
Gretna | Hawick/Harker | GRNA1 |  | 505 | 132 | CLOSED |  | OPEN
Gretna | Chapelcross No.1 | GRNA1 |  | 305 | 132 | CLOSED |  | OPEN
Gretna | Bus section | GRNA1 |  | 120 | 132 | CLOSED |  | CLOSED | close bus sections
Gretna | Chapelcross No.2 | GRNA1 |  | 205 | 132 | CLOSED |  | OPEN
Gretna | To 400kV substation | GRNA1 |  | 680 | 132 | CLOSED |  | OPEN
Gretna | Hawick | GRNA1 |  | 405 | 132 | CLOSED |  | OPEN
Gretna | Ewe hill | GRNA1 |  | 805 | 132 | CLOSED |  | OPEN
Gretna | 400kV bus bar | GRNA4 |  | X510 | 400 | CLOSED |  | OPEN
Ewe Hill WF |  | GRNA1 |  | Grid 1 | 33 | OPEN |  | OPEN
Note: The circuit breaker configuration is based on the planned GIS commissioning at Chapelcross in December 2020
Note on I8: Dieter Gutschow: Will change colour automatically if different from post blackout
Note on G29: Lauren McVey: check status of CB after blackout
Note on G31: Lauren McVey: Check Status after black start

## Restore Option 5
Restoration switching - Option 5: Sequential 33kV Restoration extending to Gretna 400kV | [18 empty] | Brkr Status
Description: | [18 empty] | OPEN
Expand from Chapelcross Gretna 400kV | [18 empty] | CLOSE
Option 5 - Builds on option 1 with additional switching to Energise Gretna 400kV and Ewe Hill WF 132kV
Restoration Actions
Stage | Transformer energisation scenario | Step | Substation Name | Circuit Breaker Operation | [6 empty] | Circuit Energised |  |  | Transformers Energised |  | Block Loads |  |  |  |  | System studies results (OK vs Fail)
|  |  |  | Busbar Name | Busbar Number | kV | Circuit | CB Number | CB action | Comment | Description | MVA | Cumulative MVA | Name (Substation, Trfr no) | MVA | Name | Max MVA | Min MVA | PF | Maximum % of DER | Load Flow Check | Voltage & Control check | Frequency response check | Transient stability check | System studies results check
Stage 1 to 4 are the restoration steps from Option 1
1 |  | 1 | Steven's Croft generator has energised up to SPD Steven's Croft 33kV interface CB | [6 empty] | Start anchor DER
|  | 1 | Connecting Steven's Croft anchor generator to Chapelcross GSP
|  | 1.1 | Steven's Croft Cust S/S |  |  | 33 | Steven's Croft SPD s/s |  | CLOSE | Cust switching.Energise SPD 33 kV busbar and earthing trfr + Load bank
|  | 1.2 | Steven's Croft SPD S/S | STCR3- | 699 | 33 | Chapelcross | tbc | CLOSE | Energise 33kV cable to Chapelcross
2 |  | 2 | Energise Chapelcross 33kV Busbars
|  | 2.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Steven's Croft 33 kV | 15 | CLOSE | Energise Chapelcross 33 kV busbars
3 |  | 3 | Restoration of Power Supply to Minsca Windfarm
|  | 3.1 | Chapelcross | CHAPA3A2 | 698 | 33 | Minsca WF | 24 | CLOSE | Energise circuit and Minsca SPD 33 kV busbar
|  | 3.2 | Minsca SPD S/S | MINS3- | 761 | 33 | Customer S/S | tbc | CLOSE | Energise customer S/S 33 kV busbar
|  | 3.3 | Minsca Customer S/S | tbc | tbc | 33 | 33 kV feeders | tbc | CLOSE | Energise cable feeders. Restore aux supply to WTGs.
No MWs from WTGs until instructed. Option to switch WTGs from voltage control mode to power factor control mode
4 |  | 4 | Restoration of Power Supply to Ewe Hill Windfarm
|  | 4.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Middlebie SWS | 12 | CLOSE | Energise circuit to Ewe Hill WF via Middlebie SWS
|  | 4.2 | Ewe Hill SPD S/S | EWHC3- | 781 | 33 | Customer S/S | 11 | CLOSE | Energise customer S/S 33 kV busbar
|  | 4.3 | Ewe Hill Customer S/S | tbc | tbc | 33 | 33 kV feeders | tbc | CLOSE | Energise cable feeders. Restore aux to WTGs.
No MWs from WTGs until instructed. Option to switch WTGs from voltage control mode to power factor control mode
Stages 5 and 6 are the additional switching required to Energise Gretna 400kV plus Ewe Hill WF 132kV
5 |  | 5.1 | Chapelcross | Chap3A1 | 698 | 33 | Chapelcross 132/33kV transformer | Grid T1 | CLOSE | Close Chapelcross Grid T1 breaker to energie 132/33kV transformer
|  | 5.2 | Chapelcross | CHAP1 | 698 | 132 | Chapelcross 132kV bus bar | 710 | CLOSE | Close Chapelcross 132kV breaker 710 to energise 132kV Busbar No.1
|  | 5.3 | Chapelcross | CHAP1 | 698 | 132 | Gretna No.1 | 1105 | CLOSE | Close Chapelcross 132kV breaker 1105 to energise circuit to Gretna
6 |  | 6.1 | Gretna | GRNA1 |  | 132 | Gretna 132kV bus bar | 305 | CLOSE | Close Gretna 132kV breaker 305 to energise Gretna 132kV bus bar
|  | 6.2 | Gretna | GRNA1 |  | 132 | Gretna 400kV SGT1 transformer | 780 | CLOSE | Close Gretna 132kV breaker 780 to energise Gretna 400kV SGT1 transformer
|  | 6.3 | Gretna | GRNA1 |  | 132 | Ewe Hill | 805 | CLOSE | Close Gretna 132kV breaker to Ewe Hill wind farm
Restore Load as per option 1 from stage 5 onwards
7 |  | 7 | Restoration of Power Supply to Annan Primary Substation. Primary restoration options A-F considered.
| A | 7.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1 and pick up block load | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12 | Annan PS | 12.12
| B | 7.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T2 | 20 | CLOSE | Ensure CB 20 to be closed in pre-restoration
| B | 7.3 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformers T1 &T2 and pick up block load | CHAPA3A1 - ANANT1 CHAPA3A2 - ANNAT2 |  |  | Annan T1 33/11kV Annan T2 33/11kV | 12 12 | Annan PS | 12.12
| B | 7.4 | Chapelcross | CHAPA3A2 | 698 | 33 | Annan No.2 | 23 | CLOSE | Restores No.2 33kV cct for security/protection purposes.
Preferred Option | C | 7.1 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T2 | 20 | CLOSE | Ensure CB 20 closed in pre-restoration
| C | 7.2 | Annan PS | ANAN5- | 662 | 11 | Bus section | 01 | OPEN | Run 2x11 kV sections (only viable if no closed 11kV rings)
| C | 7.3 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer T1 and pick up half block load | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12 | Annan PS | 6.06 tbc
| C | 7.4 | Chapelcross | CHAPA3A2 | 698 | 33 | Annan No.2 | 23 | CLOSE | Energise feeder transformer T2 and pick up half block load | CHAPA3A2 - ANANT2 |  |  | Annan T2 33/11kV | 12 | Annan PS | 6.06 tbc
| D | 7.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1 | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12
| D | 7.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Full load at Annan Primary | [5 empty] | Annan PS | 12.12
| E | 7.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1 | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12
| E | 7.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T1 | 10 | CLOSE | Take on Half load at Annan Primary | [5 empty] | Annan PS | 6.06 tbc
| E | 7.3 | Annan PS | ANAN5- | 662 | 11 | 11kV bus-section | 01 | CLOSE | Close bus-section and energise second half of the Primary load | [5 empty] | Annan PS | 6.06 tbc
| F | 7.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Annan No.1 | 13 | CLOSE | Energise feeder transformer for T1 | CHAPA3A1 - ANANT1 |  |  | Annan T1 33/11kV | 12
| F | 7.2 | Annan PS | ANAN5- | 662 | 11 | 11kV busbar for T1 | 10 | CLOSE | Energise 11kV busbar
| F | 7.3 | Annan PS | ANAN5- | 662 | 11 | 11kV feeders | tbc | CLOSE | Take on feeders one at a time | [5 empty] | Annan PS | ?
8 | A | 8 | Restoration of Power Supply to Middlebie PS
|  | 8.1 | Middlebie SWS | MIBI3- | 780 | 33 | Middlebie No.1 | 11 | CLOSE | Energise feeder transformer and pick up block load |  |  |  | Middlebie 33/11kV | 10 | Middlebie PS | 5.24
9 | A | 9 | Restoration of Power Supply to Langholm PS
|  | 9.1 | [7 empty] | Instruct Minsca WF (43 MW), Ewe Hill (12MW) , Ewe Hill 132kV WF (??) to produce 20%.
|  | 9.2 | Middlebie SWS | MIBI3- | 780 | 33 | Langholm No.1 | 14 | CLOSE | Energise feeder transformer for T1 and pick up block load | MIBI3- - LAHO3A |  |  | Langholm T1 33/11kV | 12 | Langholm PS | 6.35
10 | A | 10 | Restoration of Power Supply to Gretna PS
|  | 10.1 | Chapelcross | CHAPA3A1 | 698 | 33 | Gretna No.2 | 11 | CLOSE | Energise feeder transformer for T2 and pick up block load | CHAPA3A1 - GRNA3B |  |  | Gretna T2 33/11kV | 12 | Gretna PS | 7.1
11 | A | 11 | Restoration of Power Supply to Newcastelton PS
|  | 11.1 | Chapelcross | CHAPA3A2 | 698 | 33 | Gretna No.1, Langholm No.2, and Newcastelton. | 21 | CLOSE | Energise Newcastleton T1 and pick up block load | CHAPA3A2 - X3 X3 - GRNA3A X3 - LAHO3B |  |  | Newcastelton 33/11kV Gretna T1 33/11kV Langholm T2 33/11kV | 5 in LTDS 12 12 | Newcastelton PS | 1.09
12 | C | 12 | Restoration of Power Supply to Lockerbie PS Load 1 & 2
|  | 12.1 | [7 empty] | Instruct Minsca WF + Ewe Hill Windfarm to produce another 5%
|  | 12.2 | [7 empty] | Instruct Ewe Hill to produce another 5%
|  | 12.3 | Lockerbie | LOBI3- | 679 | 33 | 11 kV bus section | 01 | OPEN | Run 2 x 11kV sections (only viable if no closed rings) [Bus section be OPEN already]
|  | 12.4 | Chapelcross | CHAPA3A1 | 698 | 33 | Lockerbie No.1 | 14 | CLOSE | Energise Lockerbie T1 & Lockerbie Load 1. Pick up half block load. | CHAPA3A1 - X1 X1 - LOBI3A |  |  | Lockerbie T1 33/11kV | 24 | Lockerbie PS | =14.65 / 2
|  | 12.5 | [7 empty] | Instruct Minsca WF + Ewe Hill Windfarm to produce another 20%
|  | 12.6 | Chapelcross | CHAPA3A2 | 698 | 33 | Lockerbie No. 2 | 22 | CLOSE | Energise Lockerbie T2 & Lockerbie Load 2. Pick uo half block load. |  |  |  | Lockerbie T1 33/11kV | 24 | Lockerbie PS | =14.65 / 2
13 | C | 13 | Restoration of Power Supply to Kirkbank/Moffat PS Load 1
|  | 13.1 | Moffat | MOFT5- | 683 | 11 | 11kV bus section | 01 | OPEN | Run 2 x 11kV sections (only viable if no closed rings) [Bus section be OPEN already] |  |  |  | Kirkbank 33/11kV Moffat T1 33/11kV | 5 7.5 | Kirkbank PS Moffat T1 | 1.37
|  | 13.2 | Lockerbie | LOBI3A | 694 | 33 | Kirkbank & Moffat No.1 | 13 | CLOSE | Energise Moffat T1 and Load 1 and pick up block load. Delay before step 12 | LOBI3A - X4 X4 - KIBAT1 X4 - MOFTT1
14 | C | 14 | Restoration of Power Supply to Moffat PS Load 2
|  | 14.1 | Lockerbie | LOBI3A | 694 | 33 | Moffat No. 2 | 23 | CLOSE | After cold load delay, energise Moffat T2 and Load 2 and pick up block load. |  |  |  | Moffat T2 33/11kV | 7.5 | Moffat T2
15 |  | 15 | Restore network to normal operating mode to improve supply security
|  | 15.1 | Annan PS | ANAN5- | 662 | 11 | 11kV bus section | 01 | CLOSE | Close bus section to improve supply security
|  | 15.2 | Lockerbie PS | LOBI3- | 679 | 11 | 11kV bus section | 01 | CLOSE | Close bus section to improve supply security
|  | 15.3 | Moffat PS | MOFT5- | 683 | 11 | 11kV bus section | 01 | CLOSE | Close bus section to improve supply security
|  | 15.4 | Langholm | LAHO5- | 676 | 11 | Langholm T2 | 20 | CLOSE | Connect T2 to improve supply security
|  | 15.5 | Gretna | GRNA5- | 673 | 11 | Gretna T1 | 10 | CLOSE | Connect T1 to improve supply security
Note on B46: Dieter Gutschow: Option C is preferred over option A due to overloading of transformers due to cold load pickup

## CB Config Opt 2 (hidden)
Initial CB configuration in Restoration Option 2
Simultaneous 33kV Restoration (Gen + Chap BB + WFs) + Load
TO BE UPDATED | [5 empty] | status change required
| Circuit Breakers |  |  | CB Status |  |  | Comments |  | Switching required?
Substations | Name | Number | kV | Post BS | Comments | Pre-restoraton status required |  | Required
Chapelcross | Grid 1 |  | 33 | CLOSED |  | OPEN | via existing SCADA control | Open | Y
Chapelcross | Grid 2 |  | 33 | CLOSED |  | OPEN | via existing SCADA control | Open | Y
Chapelcross | Annan No.1 | 13 | 33 | OPEN | UF trip | OPEN | may want to SCADA open in case not opened | Open | Y
Chapelcross | Lockerbie No.1 | 14 | 33 | OPEN | UF trip | OPEN | may want to SCADA open in case not opened | Open | Y
Chapelcross | Middlebie SWS | 12 | 33 | CLOSED |  | OPEN | via existing SCADA control | Open | Y
Chapelcross | Gretna No.2 | 11 | 33 | CLOSED |  | OPEN | via existing SCADA control | Open
Chapelcross | Bus section | 1 | 33 | CLOSED |  | CLOSED | tbc by SCADA | Open
Chapelcross | Langholm No.2/Newcastleton | 21 | 33 | CLOSED |  | CLOSED | tbc by SCADA | Open
Chapelcross | Lockerbie No.2 | 22 | 33 | OPEN | UF trip | OPEN | may want to SCADA open in case not opened | Open
Chapelcross | Annan No.2 | 23 | 33 | OPEN | UF trip | OPEN | may want to SCADA open in case not opened | Open
Chapelcross | Minsca WF | 24 | 33 | CLOSED |  | OPEN | via existing SCADA control | Open
Stevens Croft SPD S/S | Chapelcross |  | 33 | CLOSED |  | CLOSED |  | Open | N
Stevens Croft SPD S/S | Steven's Croft |  | 33 | OPEN | via G59 | OPEN
Stevens Croft Customer S/S | SPD substation |  | 33 | OPEN | i/t from SPD G59 | OPEN | Customer's equipment
Annan 33/11kV | All 11kV CBs |  |  | OPEN |  | OPEN | Network 11kV G59 connections will be open
Lockerbie 33/11kV | Lockerbie No.1 | 12 | 33 | CLOSED |  | CLOSED
Lockerbie 33/11kV | Kirkbank/Moffat No.1 | 13 | 33 | CLOSED |  | OPEN | via existing SCADA control
Lockerbie 33/11kV | Lockerbie No.2 | 22 | 33 | CLOSED |  | CLOSED
Lockerbie 33/11kV | Moffat No.2 | 23 | 33 | CLOSED |  | CLOSED
Lockerbie 33/11kV | Bus section |  | 33 | OPEN |  | OPEN | normally open
Lockerbie 33/11kV | Grid 2 | 20 | 11 | CLOSED |  | OPEN | via existing SCADA control
Lockerbie 33/11kV | All other 11kV CBs |  | 1 | CLOSED |  | CLOSED | Network 11kV G59 connections will be open
Kirkbank 33/11kV | All 11kV CBs |  | 11 | CLOSED |  | CLOSED | Network 11kV G59 connections will be open
Moffat 33/11kV | Grid 2 | 20 | 11 | CLOSED |  | OPEN | via existing SCADA control
Moffat 33/11kV | All 11kV CBs |  | 11 | CLOSED |  | CLOSED | Network 11kV G59 connections will be open
Open
Middlebie 33kV Sw Stn | Chapelcross | 12 | 33 | CLOSED |  | CLOSED
Middlebie 33kV Sw Stn | Ewe Hill WF | 13 | 33 | CLOSED |  | CLOSED
Middlebie 33kV Sw Stn | Langholm No.1 | 14 | 33 | CLOSED |  | OPEN | via existing SCADA control
Middlebie 33kV Sw Stn | Middlebie 33/11 | 11 | 33 | CLOSED |  | OPEN | via existing SCADA control
Middlebie 33/11kV | All 11kV CBs |  | 11 | CLOSED |  | CLOSED | Network 11kV G59 connections will be open
Ewe Hill WF SPD S/S | Middlebie |  | 33 | CLOSED |  | CLOSED |  | Open | N
Ewe Hill WF SPD S/S | Ewe Hill WF |  | 33 | OPEN | via G59 | OPEN
Ewe Hill WF Customer S/S | SPD substation |  | 33 | OPEN | i/t from SPD G59 | OPEN | Customer's equipment
Langholm 33/11kV | Bus section |  | 33 | OPEN |  | OPEN | normally open
Langholm 33/11kV | Grid 2 | 20 | 11 | CLOSED |  | OPEN | via existing SCADA control
Langholm 33/11kV | All 11kV CBs |  | 11 | CLOSED |  | CLOSED | Direct & network 11kV G59 will be open
Newcastleton 33/11kV | All 11kV CBs |  | 11 | CLOSED |  | CLOSED | Direct & network 11kV G59 will be open
Gretna 33/11kV | Bus section |  | 33 | OPEN |  | OPEN | normally open
Gretna 33/11kV | Grid 1 | 10 | 11 | CLOSED |  | OPEN | via existing SCADA control
Gretna 33/11kV | All other 11kV CBs |  | 11 | CLOSED |  | CLOSED | Direct & network 11kV G59 will be open
Minsca WF SPD S/S | Chapelcross |  | 33 | CLOSED |  | CLOSED |  | Open | N
Minsca WF SPD S/S | Minsca WF |  | 33 | OPEN | via G59 | OPEN
Minsca WF Customer S/S | SPD substation |  | 33 | OPEN | i/t from SPD G59 | OPEN | Customer's equipment

## Rest Opt 2 (hidden)
Option 2 – Chapelcross GSP 33 kV Island System Restoration Plan A |  | Simultaneous 33kV Restoration (Gen + Chap BB + WFs) + Load
TO BE UPDATED
Based on CB Configuration Option 2
|  |  |  | Circuit Breaker | [5 empty] | Circuits Energised | Transformers Energised |  | Block Loads |  |  |  |  | System studies results
Stage | Step | Substation | Circuit | kV | No. | MW | kV | Cum. MVA | Action | Description | Name (Substation, Trfr no) | MVA | Name | Max MVA | Min MVA | PF | Maximum % of DER | Load Flow Check | Voltage & Control check | Frequency response check | Transient stability check | System studies results check
1
| 1.1 |  |  |  |  | 45 | 11 | 45
1.2
STCR gen has energised up to Steven's Croft 33kV interface CB
Earthing Tx switching tbc
2 |  | SPD Steven's Croft s/s to Chapelcross 33kV BB
| 2.1 | Steven's Croft 33kV | Steven's Croft gen | 33 | tbc |  |  |  | CLOSE | STCR to CHAP 33kV cable circuit
| 2.2 | Chapelcross 33kV | Steven's Croft | 33 | 15 |  |  |  | CLOSE | Chapelcross 33kV BB
Energise supplies to Minsca and Ewe Hill WFs
3
| 3.1 | Chapelcross 33kV | Minsca WF | 33 | 24 |  |  |  | CLOSE | Chap to SPD Minsca WF s/s
| 3.2 | Minsca WF 33kV | Minsca WF | 33 | tbc |  |  |  | CLOSE | 33kV interconnecting cable to WF
Minsca WF customer switching to energise wF network - load only, no MWs until instructed
| 3.3 | Chapelcross 33kV | Middlebie 33kV SwStn | 33 | 14 |  |  |  | CLOSE | Chap to Ewe Hill WF via MIBI3-
|  | Ewe Hill WF 33kV | Ewe Hill WF | 33 | tbc |  |  |  | CLOSE | 33kV interconnecting cable to WF
Minsca WF customer switching to energise wF network - load only, no MWs until instructed
Connect Primary s/s Demand
4 |  | Annan Primary | (3 options to be considered initially)
| 4.1A | Chapelcross 33kV | Annan No.1 | 33 | 13 |  |  |  | CLOSE | Annan No.1 & No.2 33kV, all 11kV | Annan T1 & T2 33/11kV | tbc | tbc
| 4.2A | Chapelcross 33kV | Annan No.2 | 33 | 23 |  |  |  | CLOSE
| 4.1B | Annan 33/11kV | Grid 2 | 11 | 20 |  |  |  | OPEN
| 4.2B | Chapelcross 33kV | Annan No.1 | 33 | 13 |  |  |  | CLOSE | Annan No.1 33kV, all 11kV | Annan T1 33/11kV | tbc | tbc
| 4.1C | Annan 33/11kV | Bus section | 11 | 1 |  |  |  | OPEN | (only vaible if no closed 11kV rings)
| 4.2C | Chapelcross 33kV | Annan No.1 | 33 | 13 |  |  |  | CLOSE | Annan No.1 33kV, ~50% 11kV | Annan T1 33/11kV | tbc
| 4.3C | Chapelcross 33kV | Annan No.2 | 33 | 23 |  |  |  | CLOSE | Annan No.2 33kV, ~50% 11kV | Annan T2 33/11kV | tbc
Langholm Primary
| 4.3 | Middlebie 33kV SW Stn | Langholm No.1 | 33 | 14 |  |  |  | CLOSE | Langholm No.1 33kV | Lang T1 33/11kV
Newcastleton Primary
| 4.4 | Chapelcross 33kV | Gretna No.1/Lang No.2/Newcastleton | 33 | 21 |  |  |  | CLOSE | Gretna No.1/Lang No.2/Newcastleton | Newcastleton T1
Newcastleton Primary
Gretna Primary
| 4.5 | Chapelcross 33kV | Gretna No.2 | 33 | 11 |  |  |  | CLOSE | Gretna No.2 | Gretna T2
Lockerbie/Kirkbank/Moffat Primaries
| 4.6 | Chapelcross 33kV | Lockerbie No.1 | 33 | 14 |  |  |  | CLOSE | Lockerbie No.1 Dumfries? | Lockerbie T1
| 4.7 | Lockerbie 33kV | Kbank/Moffat No.1 | 33 | 13 |  |  |  | CLOSE | Kirkbank/Mofat No.1 33kV | Kirkbank T1, Moffat T1

## Rest Opt 3 (hidden)
Option 3 – Chapelcross GSP 33 kV Island System Restoration Plan A |  | Chapelcross 132/33kV Tx (3A - sequential incl Ecclefecan, 3B sequential excl Ecclfecan, 3C Simultaneous incl Ecclfechan, 3D Simulatneous excl Ecclefechan)
TO BE UPDATED
Based on CB Configuration Option 2
|  |  |  | Circuit Breaker | [5 empty] | Circuits Energised | Transformers Energised |  | Block Loads |  |  |  |  | System studies results
Stage | Step | Substation | Circuit | kV | No. | MW | kV | Cum. MVA | Action | Description | Name (Substation, Trfr no) | MVA | Name | Max MVA | Min MVA | PF | Maximum % of DER | Load Flow Check | Voltage & Control check | Frequency response check | Transient stability check | System studies results check
1
| 1.1 |  |  |  |  | 45 | 11 | 45
1.2
STCR gen has energised up to Steven's Croft 33kV interface CB
Earthing Tx switching tbc
2 |  | SPD Steven's Croft s/s to Chapelcross 33kV BB
| 2.1 | Steven's Croft 33kV | Steven's Croft gen | 33 | tbc |  |  |  | CLOSE | STCR to CHAP 33kV cable circuit
| 2.2 | Chapelcross 33kV | Steven's Croft | 33 | 15 |  |  |  | CLOSE | Chapelcross 33kV BB
Energise supplies to Minsca and Ewe Hill WFs
3
| 3.1 | Chapelcross 33kV | Minsca WF | 33 | 24 |  |  |  | CLOSE | Chap to SPD Minsca WF s/s
| 3.2 | Minsca WF 33kV | Minsca WF | 33 | tbc |  |  |  | CLOSE | 33kV interconnecting cable to WF
Minsca WF customer switching to energise wF network - load only, no MWs until instructed
| 3.3 | Chapelcross 33kV | Middlebie 33kV SwStn | 33 | 14 |  |  |  | CLOSE | Chap to Ewe Hill WF via MIBI3-
|  | Ewe Hill WF 33kV | Ewe Hill WF | 33 | tbc |  |  |  | CLOSE | 33kV interconnecting cable to WF
Minsca WF customer switching to energise wF network - load only, no MWs until instructed
Connect Primary s/s Demand
4 |  | Annan Primary | (3 options to be considered initially)
| 4.1A | Chapelcross 33kV | Annan No.1 | 33 | 13 |  |  |  | CLOSE | Annan No.1 & No.2 33kV, all 11kV | Annan T1 & T2 33/11kV | tbc | tbc
| 4.2A | Chapelcross 33kV | Annan No.2 | 33 | 23 |  |  |  | CLOSE
| 4.1B | Annan 33/11kV | Grid 2 | 11 | 20 |  |  |  | OPEN
| 4.2B | Chapelcross 33kV | Annan No.1 | 33 | 13 |  |  |  | CLOSE | Annan No.1 33kV, all 11kV | Annan T1 33/11kV | tbc | tbc
| 4.1C | Annan 33/11kV | Bus section | 11 | 1 |  |  |  | OPEN | (only vaible if no closed 11kV rings)
| 4.2C | Chapelcross 33kV | Annan No.1 | 33 | 13 |  |  |  | CLOSE | Annan No.1 33kV, ~50% 11kV | Annan T1 33/11kV | tbc
| 4.3C | Chapelcross 33kV | Annan No.2 | 33 | 23 |  |  |  | CLOSE | Annan No.2 33kV, ~50% 11kV | Annan T2 33/11kV | tbc
Langholm Primary
| 4.3 | Middlebie 33kV SW Stn | Langholm No.1 | 33 | 14 |  |  |  | CLOSE | Langholm No.1 33kV | Lang T1 33/11kV
Newcastleton Primary
| 4.4 | Chapelcross 33kV | Gretna No.1/Lang No.2/Newcastleton | 33 | 21 |  |  |  | CLOSE | Gretna No.1/Lang No.2/Newcastleton | Newcastleton T1
Newcastleton Primary
Gretna Primary
| 4.5 | Chapelcross 33kV | Gretna No.2 | 33 | 11 |  |  |  | CLOSE | Gretna No.2 | Gretna T2
Lockerbie/Kirkbank/Moffat Primaries
| 4.6 | Chapelcross 33kV | Lockerbie No.1 | 33 | 14 |  |  |  | CLOSE | Lockerbie No.1 Dumfries? | Lockerbie T1
| 4.7 | Lockerbie 33kV | Kbank/Moffat No.1 | 33 | 13 |  |  |  | CLOSE | Kirkbank/Mofat No.1 33kV | Kirkbank T1, Moffat T1

## Rest Opt 4 (hidden)
Option 4 – Chapelcross GSP 33 kV Island System Restoration Plan A |  | Expand from Chapelcross 132kV to Dumfries
TO BE UPDATED
Based on CB Configuration Option 2
|  |  |  | Circuit Breaker | [5 empty] | Circuits Energised | Transformers Energised |  | Block Loads |  |  |  |  | System studies results
Stage | Step | Substation | Circuit | kV | No. | MW | kV | Cum. MVA | Action | Description | Name (Substation, Trfr no) | MVA | Name | Max MVA | Min MVA | PF | Maximum % of DER | Load Flow Check | Voltage & Control check | Frequency response check | Transient stability check | System studies results check
1
| 1.1 |  |  |  |  | 45 | 11 | 45
1.2
STCR gen has energised up to Steven's Croft 33kV interface CB
Earthing Tx switching tbc
2 |  | SPD Steven's Croft s/s to Chapelcross 33kV BB
| 2.1 | Steven's Croft 33kV | Steven's Croft gen | 33 | tbc |  |  |  | CLOSE | STCR to CHAP 33kV cable circuit
| 2.2 | Chapelcross 33kV | Steven's Croft | 33 | 15 |  |  |  | CLOSE | Chapelcross 33kV BB
Energise supplies to Minsca and Ewe Hill WFs
3
| 3.1 | Chapelcross 33kV | Minsca WF | 33 | 24 |  |  |  | CLOSE | Chap to SPD Minsca WF s/s
| 3.2 | Minsca WF 33kV | Minsca WF | 33 | tbc |  |  |  | CLOSE | 33kV interconnecting cable to WF
Minsca WF customer switching to energise wF network - load only, no MWs until instructed
| 3.3 | Chapelcross 33kV | Middlebie 33kV SwStn | 33 | 14 |  |  |  | CLOSE | Chap to Ewe Hill WF via MIBI3-
|  | Ewe Hill WF 33kV | Ewe Hill WF | 33 | tbc |  |  |  | CLOSE | 33kV interconnecting cable to WF
Minsca WF customer switching to energise wF network - load only, no MWs until instructed
Connect Primary s/s Demand
4 |  | Annan Primary | (3 options to be considered initially)
| 4.1A | Chapelcross 33kV | Annan No.1 | 33 | 13 |  |  |  | CLOSE | Annan No.1 & No.2 33kV, all 11kV | Annan T1 & T2 33/11kV | tbc | tbc
| 4.2A | Chapelcross 33kV | Annan No.2 | 33 | 23 |  |  |  | CLOSE
| 4.1B | Annan 33/11kV | Grid 2 | 11 | 20 |  |  |  | OPEN
| 4.2B | Chapelcross 33kV | Annan No.1 | 33 | 13 |  |  |  | CLOSE | Annan No.1 33kV, all 11kV | Annan T1 33/11kV | tbc | tbc
| 4.1C | Annan 33/11kV | Bus section | 11 | 1 |  |  |  | OPEN | (only vaible if no closed 11kV rings)
| 4.2C | Chapelcross 33kV | Annan No.1 | 33 | 13 |  |  |  | CLOSE | Annan No.1 33kV, ~50% 11kV | Annan T1 33/11kV | tbc
| 4.3C | Chapelcross 33kV | Annan No.2 | 33 | 23 |  |  |  | CLOSE | Annan No.2 33kV, ~50% 11kV | Annan T2 33/11kV | tbc
Langholm Primary
| 4.3 | Middlebie 33kV SW Stn | Langholm No.1 | 33 | 14 |  |  |  | CLOSE | Langholm No.1 33kV | Lang T1 33/11kV
Newcastleton Primary
| 4.4 | Chapelcross 33kV | Gretna No.1/Lang No.2/Newcastleton | 33 | 21 |  |  |  | CLOSE | Gretna No.1/Lang No.2/Newcastleton | Newcastleton T1
Newcastleton Primary
Gretna Primary
| 4.5 | Chapelcross 33kV | Gretna No.2 | 33 | 11 |  |  |  | CLOSE | Gretna No.2 | Gretna T2
Lockerbie/Kirkbank/Moffat Primaries
| 4.6 | Chapelcross 33kV | Lockerbie No.1 | 33 | 14 |  |  |  | CLOSE | Lockerbie No.1 Dumfries? | Lockerbie T1
| 4.7 | Lockerbie 33kV | Kbank/Moffat No.1 | 33 | 13 |  |  |  | CLOSE | Kirkbank/Mofat No.1 33kV | Kirkbank T1, Moffat T1

## Rest Opt 5 (hidden)
Option 4 – Chapelcross GSP 33 kV Island System Restoration Plan A |  | Expand from Chapelcross 132kV to Gretna
TO BE UPDATED
Based on CB Configuration Option 2
|  |  |  | Circuit Breaker | [5 empty] | Circuits Energised | Transformers Energised |  | Block Loads |  |  |  |  | System studies results
Stage | Step | Substation | Circuit | kV | No. | MW | kV | Cum. MVA | Action | Description | Name (Substation, Trfr no) | MVA | Name | Max MVA | Min MVA | PF | Maximum % of DER | Load Flow Check | Voltage & Control check | Frequency response check | Transient stability check | System studies results check
1
| 1.1 |  |  |  |  | 45 | 11 | 45
1.2
STCR gen has energised up to Steven's Croft 33kV interface CB
Earthing Tx switching tbc
2 |  | SPD Steven's Croft s/s to Chapelcross 33kV BB
| 2.1 | Steven's Croft 33kV | Steven's Croft gen | 33 | tbc |  |  |  | CLOSE | STCR to CHAP 33kV cable circuit
| 2.2 | Chapelcross 33kV | Steven's Croft | 33 | 15 |  |  |  | CLOSE | Chapelcross 33kV BB
Energise supplies to Minsca and Ewe Hill WFs
3
| 3.1 | Chapelcross 33kV | Minsca WF | 33 | 24 |  |  |  | CLOSE | Chap to SPD Minsca WF s/s
| 3.2 | Minsca WF 33kV | Minsca WF | 33 | tbc |  |  |  | CLOSE | 33kV interconnecting cable to WF
Minsca WF customer switching to energise wF network - load only, no MWs until instructed
| 3.3 | Chapelcross 33kV | Middlebie 33kV SwStn | 33 | 14 |  |  |  | CLOSE | Chap to Ewe Hill WF via MIBI3-
|  | Ewe Hill WF 33kV | Ewe Hill WF | 33 | tbc |  |  |  | CLOSE | 33kV interconnecting cable to WF
Minsca WF customer switching to energise wF network - load only, no MWs until instructed
Connect Primary s/s Demand
4 |  | Annan Primary | (3 options to be considered initially)
| 4.1A | Chapelcross 33kV | Annan No.1 | 33 | 13 |  |  |  | CLOSE | Annan No.1 & No.2 33kV, all 11kV | Annan T1 & T2 33/11kV | tbc | tbc
| 4.2A | Chapelcross 33kV | Annan No.2 | 33 | 23 |  |  |  | CLOSE
| 4.1B | Annan 33/11kV | Grid 2 | 11 | 20 |  |  |  | OPEN
| 4.2B | Chapelcross 33kV | Annan No.1 | 33 | 13 |  |  |  | CLOSE | Annan No.1 33kV, all 11kV | Annan T1 33/11kV | tbc | tbc
| 4.1C | Annan 33/11kV | Bus section | 11 | 1 |  |  |  | OPEN | (only vaible if no closed 11kV rings)
| 4.2C | Chapelcross 33kV | Annan No.1 | 33 | 13 |  |  |  | CLOSE | Annan No.1 33kV, ~50% 11kV | Annan T1 33/11kV | tbc
| 4.3C | Chapelcross 33kV | Annan No.2 | 33 | 23 |  |  |  | CLOSE | Annan No.2 33kV, ~50% 11kV | Annan T2 33/11kV | tbc
Langholm Primary
| 4.3 | Middlebie 33kV SW Stn | Langholm No.1 | 33 | 14 |  |  |  | CLOSE | Langholm No.1 33kV | Lang T1 33/11kV
Newcastleton Primary
| 4.4 | Chapelcross 33kV | Gretna No.1/Lang No.2/Newcastleton | 33 | 21 |  |  |  | CLOSE | Gretna No.1/Lang No.2/Newcastleton | Newcastleton T1
Newcastleton Primary
Gretna Primary
| 4.5 | Chapelcross 33kV | Gretna No.2 | 33 | 11 |  |  |  | CLOSE | Gretna No.2 | Gretna T2
Lockerbie/Kirkbank/Moffat Primaries
| 4.6 | Chapelcross 33kV | Lockerbie No.1 | 33 | 14 |  |  |  | CLOSE | Lockerbie No.1 Dumfries? | Lockerbie T1
| 4.7 | Lockerbie 33kV | Kbank/Moffat No.1 | 33 | 13 |  |  |  | CLOSE | Kirkbank/Mofat No.1 33kV | Kirkbank T1, Moffat T1

## Option 2 (hidden)
Option 2 – Chapelcross GSP 33 kV Island System Restoration Plan B
|  | System Restoration Plan | [6 empty] | DER connected |  |  |  |  | Transformers Energised |  |  | Circuits energised |  |  | Block Loads |  |  |  |  | System studies results
Stage | Step | Restoration Description | Locations | Network switching operation and control actions | Description | Sending BB (e.g. CHAP3-) | Receiving BB (e.g. STCR3-) | CB closed (e.g. CHAP3-11) | Name | MVA | MW | kV | Cum. MVA | Name (Substation, Trfr no) | MVA | Inrush Current (Inrush/Irated) | Circuit Name (Source - Destination) | Length (km) | Charging Power (MVAr) | Name | Maximum MVA | Minimum MVA | PF | Maximum % of DER | Load Flow Check | Voltage & Control check | Frequency response check | Transient stability check | System studies results check
1 |  | Starting up Stevens Croft anchor DER | [7 empty] | 59.68
| 1.1 | Start Stevens Croft anchor DER |  | Maintain acceptable unit voltage and speed | [6 empty] | 45 | 11 | 45
| 1.2 | Pick up auxiliary load | Stevens Croft | Switch 11 kV CB for site auxiliary transformer | [15 empty] | Stevens Croft AL | 3.5 | 1.5 | 1 | 5.865%
| 1.3 | Energise unit step up transformer | Stevens Croft | Switch 11 kV CB for the unit step-up transformer | [9 empty] | DER step up transformer | 50
| 1.4 | Energise the site 33 kV busbar | Stevens Croft | Switch 33 kV CB for the unit step-up transformer
| 1.5 | Energise the SPD 33 kV busbar | Stevens Croft | Switch 33 kV CB to the SPD substation
| 1.6 | Control system voltage if necessary | Stevens Croft | Adjust V-setting point for Stevens Croft DER
| 1.7 | Control system frequency if necessary | Stevens Croft | Adjust F-setting point for Stevens Croft DER
2 |  | Energisation of Chapelcross GSP 33kV busbar
| 2.1 | Energize the 33 kV cable circuit | Stevens Croft | Switch 33 kV CB on Stevens Croft side of the circuit | [12 empty] | Stevens Croft - Chapelcross GSP
| 2.2 | Energise Chapelcross first 33 kV busbar | Chapelcross GSP | Switch 33 kV CB on Chapelcross side of the circuit | [12 empty] | Stevens Croft - Chapelcross GSP
| 2.3 | Energise Chapelcross second 33 kV busbar | Chapelcross GSP | Switch 33kV busbar coupler
3 |  | Connection of MINSCA WF to Chapelcross GSP network | [7 empty] | 37
| 3.1 | Energise the circuit to MINSCA WF | Chapelcross GSP | Switch 33 kV CB on Chapelcross side of the circuit | [12 empty] | Chapelcross GSP - MINSCA WF
| 3.2 | Energise the 33 kV busbar at the WF SPD substation | MINSCA WF (SPD) | Switch 33 kV CB on MINSCA WF side of the circuit | [12 empty] | Chapelcross GSP - MINSCA WF
| 3.3 | Energise the 33 kV busbar at the WF substation (POC) | MINSCA WF (SPD) | Switch 33 kV CB for the circuit to WF POC
| 3.4 | Energise WF transformers and connect MINSCA WF | MINSCA WF | Switch 33 kV CB or CBs to MINSCA WF | [9 empty] | MINSCA WF | 44.4
| 3.5 | Control system voltage if necessary | MINSCA WF | Adjust V-setting point and control mode for MINSCA WF
| 3.6 | Control system frequency if necessary | MINSCA WF | Adjust F-setting point and control mode for MINSCA WF
4 |  | Restoration of power supply to Annan PS
| 4.1 | Energise transformer feeder 1 | Chapelcross GSP | Switch 33 kV CB to Annan PS T1 | [9 empty] | Annan 33/11 kV T1 | 12 |  | Chapelcross - Annan 1
|  | Energise transformer feeder 2 | Chapelcross GSP | [10 empty] | Annan 33/11 kV T2 | 12 |  | Chapelcross - Annan 2
|  | Pick up block load at Annan PS automatically | Annan PS | [16 empty] | Annan PS | 12.12 |  |  | 20.31%
| 4.2 | Form double supply loop to Annan PS | Chapelcross GSP | Switch 33 kV CB to Annan PS T2
| 4.3 | Control system voltage if necessary | Stevens Croft | Adjust V-setting point for Stevens Croft DER
| 4.4 | Control system frequency if necessary | Stevens Croft | Adjust F-setting point for Stevens Croft DER
5 |  | Restoration of power supply to Middlebie PS
| 5.1 | Energise the circuit to Middlebie SWS | Chapelcross GSP | Switch 33 kV CB on Chapelcross GSP side of the circuit | [12 empty] | Chapelcross GSP - Middlebie SWS
| 5.2 | Energise Middlebie SWS busbar | Middlebie SWS | Switch 33 kV CB to Middlebie SWS side of the circuit | [12 empty] | Chapelcross GSP - Middlebie SWS
| 5.3 | Energise transformer feeder to Middlebie PS | Middlebie SWS | Switch 33 kV CB to Middlebie 33/11 kV transformer | [9 empty] | Middlebie 33/11 kV T1 | 10
|  | Pick up block load at Middlebie PS automatically | Middlebie PS | [16 empty] | Middlebie PS | 5.24 |  |  | 8.78%
| 5.4 | Control system voltage if necessary | Stevens Croft | Adjust V-setting point for Stevens Croft DER
| 5.5 | Control system frequency if necessary | Stevens Croft | Adjust F-setting point for Stevens Croft DER
6 |  | Connection of EWE HILL WF to Chapelcross GSP network | [7 empty] | 12
| 6.1 | Energise the circuit to EWE HILL WF | Middlebie SWS | Switch 33 kV CB on Middlebie SWS side of the circuit | [12 empty] | Middlebie SWS - EWE HILL WF
| 6.2 | Energise the 33 kV busbar at the WF SPD substation | EWE HILL WF (SPD) | Switch 33 kV CB on EWE HILL WF side of the circuit | [12 empty] | Middlebie SWS - EWE HILL WF
| 6.3 | Energise the 33 kV busbar at the WF substation (POC) | EWE HILL WF (SPD) | Switch 33 kV CB for the circuit to WF POC
| 6.4 | Energise WF transformers and connect EWE HILL WF | EWE HILL WF | Switch 33 kV CB or CBs to EWE HILL WF | [9 empty] | EWE HILL WF | 13
| 6.5 | Control system voltage if necessary | EWE HILL WF | Adjust V-setting point and control mode for EWE HILL WF
| 6.6 | Control system frequency if necessary | EWE HILL WF | Adjust F-setting point and control mode for EWE HILL WF
7 |  | Restoration of power supply to Langholm, Newcastelton and Gretna PS
| 7.1 | Energise the transformer feeder to Gretna A | Chapelcross GSP | Switch 33 kV CB on Chapelcross side of the circuit | [9 empty] | Gretna 33/11 kV T1 | 12 |  | Chapelcross GSP - Gretna A -
|  | Energise the transformer feeder to Gretna B | Chapelcross GSP | [10 empty] | Gretna 33/11 kV T2 | 12 |  | Chapelcross GSP - Gretna B
|  | Energise the transformer feeder to Langholm B | Chapelcross GSP | [10 empty] | Langholm 33/11 kV T2 | 12 |  | Chapelcross GSP - Langholm B
|  | Energise the transformer feeder to Langholm A | Chapelcross GSP | [10 empty] | Langholm 33/11 kV T1 | 12 |  | Middlebie SWS - Langholm A
|  | Energise transformer feeder to Newcastelton | Chapelcross GSP | [10 empty] | Newcastelton 33/11 kV T1 | 5 |  | Langholm B - Newcastelton
|  | Pick up block load at Gretna PS automatically | Gretna PS | [16 empty] | Gretna PS | 7.1 |  |  | 11.9%
|  | Pick up block load at Langholm PS automatically | Langholm PS | [16 empty] | Langholm PS | 6.35 |  |  | 10.64%
|  | Pick up block load at Newcastelton PS automatically | Newcastelton PS | [16 empty] | Newcastelton PS | 1.09 |  |  | 1.826%
[20 empty] | Total block load | 14.54 |  |  | 24.36%
| 7.2 | Form double supply loop to Gretna PS | Chapelcross GSP | Switch 33 kV CB on Chapelcross side of the circuit | [12 empty] | Chapelcross GSP - Gretna B
| 7.3 | Form double supply loop to Langholm PS | Middlebie SWS | Switch 33 kV CB on Langholm side of the circuit | [12 empty] | Middlebie SWS - Langholm A
| 7.4 | Control system voltage if necessary | Stevens Croft | Adjust V-setting point for Stevens Croft DER
| 7.5 | Control system frequency if necessary | Stevens Croft | Adjust F-setting point for Stevens Croft DER
| 7.6 | Maintain NOP's at Gretna PS | Gretna | Switch / Maintain NOP CB's open
| 7.7 | Maintain NOP's at Langholm PS | Langholm | Switch / Maintain NOP CB's open
8 |  | Connection of CRAIG and CRAIG II WF to Chapelcross GSP network | [7 empty] | 10
| 8.1 | Energise the circuit to Craig WF | Langholm PS | Switch 11 kV CB on Langholm PS side of the circuit | [12 empty] | Langholm PS - Craig WF
| 8.2 | Energise the circuit to Craig II WF | Langholm PS | Switch 11 kV CB on Langholm PS side of the circuit | [12 empty] | Langholm PS - Craig II WF
| 8.3 | Energise the 11 kV busbar at Craig WF | Craig WF | Switch 11 kV CB on Craig WF side of the circuit | [12 empty] | Langholm PS - Craig WF
| 8.4 | Energise the 11 kV busbar at Craig II WF | Craig II WF | Switch 11 kV CB on Craig II WF side of the circuit | [12 empty] | Langholm PS - Craig II WF
| 8.5 | Energise WF transformers and connect Craig WF | Craig WF | Switch 11 kV CB or CBs to Craig WF | [9 empty] | Craig WF | ??
| 8.6 | Energise WF transformers and connect Craig II WF | Craig II WF | Switch 11 kV CB or CBs to Craig II WF | [9 empty] | Craig II WF | ??
| 8.7 | Control system voltage if necessary | Craig WF | Adjust V-setting point and control mode for EWE HILL WF
| 8.8 | Control system frequency if necessary | Craig II WF | Adjust F-setting point and control mode for EWE HILL WF
9 |  | Restoration of power supply to Lockerbie, Kirkbank and Moffat PS
| 9.1 | Energise transformer feeder to Lockerbie A | Chapelcross GSP | Switch 33 kV CB on Chapelcross side of the circuit | [9 empty] | Lockerbie A 33/11 kV T1 | 24 |  | Chapelcross GSP - Lockerbie A
|  | Energise transformer feeder to Lockerbie B | Chapelcross GSP | [10 empty] | Lockerbie B 33/11 kV T2 | 24 |  | Chapelcross GSP - Lockerbie B
|  | Energise transformer feeder to Kirkbank | Chapelcross GSP | [10 empty] | Kirkbank 33/11 kV T1 | 5 |  | Lockerbie A - Kirkbank
|  | Energise transformer feeder 1 to Moffat | Chapelcross GSP | [10 empty] | Moffat 33/11 kV T1 | 10 |  | Kirkbank - Moffat T1
|  | Energise transformer feeder 2 to Moffat | Chapelcross GSP | [10 empty] | Moffat 33/11 kV T2 | 10 |  | Lockerbie B - Moffat T2
|  | Energise Carrutherstown sector 414 (first half 33 kV busbar) | Chapelcross GSP | [13 empty] | Chapelcross GSP X1 - Carrutherstown
|  | Pick up block load at Lockerbie PS automatically | Lockerbie PS | [16 empty] | Lockerbie PS | 14.65 |  |  | 24.55% | 14.65
|  | Pick up block load at Kirkbank PS automatically | Kirkbank PS | [16 empty] | Langholm PS | 6.35 |  |  | 10.64% | 6.35
|  | Pick up block load at Moffat PS automatically | Moffat PS | [16 empty] | Newcastelton PS | 1.09 |  |  | 1.826% | 1.09
[20 empty] | Total block load | 22.09 |  |  | 37.01% | 22.09
| 9.2 | Form double supply loop to Lockerbie PS | Chapelcross GSP | Switch 33 kV CB on Chapelcross side of the circuit | [12 empty] | Chapelcross GSP - Lockerbie B
| 9.3 | Control system voltage if necessary | Stevens Croft | Adjust V-setting point for Stevens Croft DER
| 9.4 | Control system frequency if necessary | Stevens Croft | Adjust F-setting point for Stevens Croft DER
| 9.5 | Maintain NOP's at Lockerbie PS | Lockerbie | Switch / Maintain NOP CB's open

## Option 3 (hidden)
Option 3 – Chapelcross GSP 33 kV Island System Restoration Plan C
|  | System Restoration Plan | [6 empty] | DER connected |  |  |  |  | Transformers Energised |  |  | Circuits energised |  |  | Block Loads |  |  |  |  | System studies results
Stage | Step | Restoration Description | Locations | Network switching operation and control actions | Description | Sending BB (e.g. CHAP3-) | Receiving BB (e.g. STCR3-) | CB closed (e.g. CHAP3-11) | Name | MVA | MW | kV | Cum. MVA | Name (Substation, Trfr no) | MVA | Inrush Current (Inrush/Irated) | Circuit Name (Source - Destination) | Length (km) | Charging Power (MVAr) | Name | Maximum MVA | Minimum MVA | PF | Maximum % of DER | Load Flow Check | Voltage & Control check | Frequency response check | Transient stability check | System studies results check
1 |  | Switching operation at Chapelcross GSP if necessary
| 1.1 | Enable CB status "on" for busbar coupler | Chapelcross GSP | Switch 33kV busbar coupler
| 1.2 | Enable CB status "on" for circuit to Stevens Croft | Chapelcross GSP | Switch 33 kV CB on Chapelcross side of the circuit | [12 empty] | Stevens Croft - Chapelcross GSP
| 1.3 | Enable CB status "on" for circuit to MINSCA WF | Chapelcross GSP | Switch 33 kV CB on Chapelcross side of the circuit | [12 empty] | Chapelcross GSP - MINSCA WF
| 1.4 | Enable CB status "on" for circuit to Middlebie SWS | Chapelcross GSP | Switch 33 kV CB on Chapelcross GSP side of the circuit | [12 empty] | Chapelcross GSP - Middlebie SWS
| 1.5 | Enable CB status "on" for circuit to Annan PS T1 | Chapelcross GSP | Switch 33 kV CB to Annan PS T1 | [12 empty] | Chapelcross - Annan 1
| 1.6 | Enable CB status "on" for circuit to Annan PS T2 | Chapelcross GSP | Switch 33 kV CB to Annan PS T2 | [12 empty] | Chapelcross - Annan 2
| 1.7 | Enable CB status "on" for circuit to Gretna 33/11 kV PT1 | Chapelcross GSP | Switch 33 kV CB on Chapelcross side of the circuit | [12 empty] | Chapelcross GSP - Gretna A
| 1.8 | Enable CB status "on" for circuit to Gretna 33/11 kV PT2 | Chapelcross GSP | Switch 33 kV CB on Chapelcross side of the circuit | [12 empty] | Chapelcross GSP - Gretna B
| 1.9 | Enable CB status "on" for circuit to Lockerbie A | Chapelcross GSP | Switch 33 kV CB on Chapelcross side of the circuit | [12 empty] | Chapelcross GSP - Lockerbie A
| 1.10 | Enable CB status "on" for circuit to Lockerbie B | Chapelcross GSP | Switch 33 kV CB on Chapelcross side of the circuit | [12 empty] | Chapelcross GSP - Lockerbie B
2 |  | Switching operation at Middlebie SWS if necessary
| 2.1 | Enable CB status "on" for circuit to Chapelcross GSP | Middlebie SWS | Switch 33 kV CB on Middlebie SWS side of the circuit | [12 empty] | Chapelcross GSP - Middlebie SWS
| 2.2 | Enable CB status "on" for circuit to EWE HILL WF | Middlebie SWS | Switch 33 kV CB on Middlebie SWS side of the circuit | [12 empty] | Middlebie SWS - EWE HILL WF
| 2.3 | Enable CB status "on" for circuit to Middlebie PS | Middlebie SWS | Switch 33 kV CB to Middlebie 33/11 kV transformer
| 2.4 | Enable CB status "on" for circuit to Langholm T1 | Middlebie SWS | Switch 33 kV CB on Langholm side of the circuit | [12 empty] | Middlebie SWS - Langholm A
3 |  | Switching operation at 33 kV NOP if necessary
| 3.1 | Maintain NOP's at Gretna PS | Gretna | Switch / Maintain NOP CB's open
| 3.2 | Maintain NOP's at Langholm PS | Langholm | Switch / Maintain NOP CB's open
| 3.3 | Maintain NOP's at Lockerbie PS | Lockerbie | Switch / Maintain NOP CB's open
4 |  | Switching operation at Primary Substations if necessary
| 4.1A | Enable CB status "on" for circuit to Annan PS T1 | Annan PS | Switch 11 kV CB to Annan PS T1
| 4.1B | Enable CB status "on" for circuit to Annan PS T2 | Annan PS | Switch 11 kV CB to Annan PS T2
| 4.1C | Enable CB status "off" for all feeders to Annan PS | Annan PS | Switch 11 kV CB to all 11 kV feeders
| 4.2A | Enable CB status "on" for circuit to Middlebie PS T1 | Middlebie PS | Switch 11 kV CB to Middlebie PS T1
| 4.2B | Enable CB status "off" for all feeders to Middlebie PS | Middlebie PS | Switch 11 kV CB to all 11 kV feeders
| 4.3A | Enable CB status "on" for circuit to Langholm PS T1 | Langholm PS | Switch 11 kV CB to Langholm PS T1
| 4.3B | Enable CB status "on" for circuit to Langholm PS T2 | Langholm PS | Switch 11 kV CB to Langholm PS T2
| 4.3C | Enable CB status "off" for all feeders to Langholm PS | Langholm PS | Switch 11 kV CB to all 11 kV feeders
| 4.4A | Enable CB status "on" for circuit to Newcastelton PS T1 | Newcastelton PS | Switch 11 kV CB to Newcastelton PS T1
| 4.4B | Enable CB status "off" for all feeders to Newcastelton PS | Newcastelton PS | Switch 11 kV CB to all 11 kV feeders
| 4.5A | Enable CB status "on" for circuit to Gretna PS T1 | Gretna PS | Switch 11 kV CB to Gretna PS T1
| 4.5B | Enable CB status "on" for circuit to Gretna PS T2 | Gretna PS | Switch 11 kV CB to Gretna PS T2
| 4.5C | Enable CB status "off" for all feeders to Gretna PS | Gretna PS | Switch 11 kV CB to all 11 kV feeders
| 4.6A | Enable CB status "on" for circuit to Lockerbie PS T1 | Lockerbie PS | Switch 11 kV CB to Lockerbie PS T1
| 4.6B | Enable CB status "on" for circuit to Lockerbie PS T2 | Lockerbie PS | Switch 11 kV CB to Lockerbie PS T2
| 4.6C | Enable CB status "off" for all feeders to Lockerbie PS | Lockerbie PS | Switch 11 kV CB to all 11 kV feeders
| 4.7A | Enable CB status "on" for circuit to Kirkbank PS T1 | Kirkbank PS | Switch 11 kV CB to Kirkbank PS T1
| 4.7B | Enable CB status "off" for all feeders to Kirkbank PS | Kirkbank PS | Switch 11 kV CB to all 11 kV feeders
| 4.8A | Enable CB status "on" for circuit to Moffat PS T1 | Moffat PS | Switch 11 kV CB to Moffat PS T1
| 4.8B | Enable CB status "on" for circuit to Moffat PS T2 | Moffat PS | Switch 11 kV CB to Moffat PS T2
| 4.8C | Enable CB status "off" for all feeders to Moffat PS | Moffat PS | Switch 11 kV CB to all 11 kV feeders
5 |  | Starting up Stevens Croft anchor DER
| 5.1 | Start Stevens Croft anchor DER |  | Maintain acceptable unit voltage and speed | [6 empty] | 45 | 11 | 45
| 5.2 | Energise unit step up transformer | Stevens Croft | Switch 11 kV CB for the unit step-up transformer | [9 empty] | DER step up transformer | 53
| 5.3 | Energise the site 33 kV busbar | Stevens Croft | Switch 33 kV CB for the unit step-up transformer
| 5.4 | Energise the SPD 33 kV busbar | Stevens Croft | Switch 33 kV CB to the SPD substation
6 |  | Energisation of Chapelcross GSP 33kV busbar
| 6.1 | Energize the 33 kV cable circuit | Stevens Croft | Switch 33 kV CB on Stevens Croft side of the circuit | [12 empty] | Stevens Croft - Chapelcross GSP
|  | Energize the 33 kV Chapelcross GSP 33 kV busbar automatically | Chapelcross GSP
|  | Energize the 33 kV feeder and Annan PS T1 automatically | Annan PS | [10 empty] | Annan 33/11 kV T1 | 12
|  | Energize the 33 kV feeder and Annan PS T2 automatically | Annan PS | [10 empty] | Annan 33/11 kV T2 | 12
|  | Energize the 33 kV feeder to Middlebie SWS automatically | Middlebie SWS
|  | Energize Middlebie PS T1 automatically | Middlebie | [10 empty] | Middlebie 33/11 kV T1 | 10
|  | Energize the 33 kV feeder to Langholm PS T1 automatically | Langholm PS | [10 empty] | Langholm 33/11 kV T1 | 12
|  | Energize the 33 kV feeder to Langholm PS T2 automatically | Langholm PS | [10 empty] | Langholm 33/11 kV T2 | 12
|  | Energize the 33 kV feeder to Newcastelton PS T1 automatically | Newcastelton PS | [10 empty] | Newcastelton 33/11 kV T1 | 5
|  | Energize the 33 kV feeder to Gretna PS T1 automatically | Gretna PS | [10 empty] | Gretna 33/11 kV T1 | 12
|  | Energize the 33 kV feeder to Gretna PS T2 automatically | Gretna PS | [10 empty] | Gretna 33/11 kV T2 | 12
|  | Energize the 33 kV feeder to Lockerbie PS T1 automatically | Lockerbie PS | [10 empty] | Lockerbie A 33/11 kV T1 | 24
|  | Energize the 33 kV feeder to Lockerbie PS T2 automatically | Lockerbie PS | [10 empty] | Lockerbie B 33/11 kV T2 | 24
|  | Energize the 33 kV feeder to Kirkbank PS T1 automatically | Kirkbank PS | [10 empty] | Kirkbank 33/11 kV T1 | 5
|  | Energize the 33 kV feeder to Moffat PS T1 automatically | Moffat PS | [10 empty] | Moffat 33/11 kV T1 | 7.5
|  | Energize the 33 kV feeder to Moffat PS T2 automatically | Moffat PS | [10 empty] | Moffat 33/11 kV T2 | 7.5
| 6.2 | Control system voltage if necessary | Stevens Croft | Adjust V-setting point for Stevens Croft DER
| 6.3 | Control system frequency if necessary | Stevens Croft | Adjust F-setting point for Stevens Croft DER
| 6.4 | Pick up auxiliary load at Stevens Croft | Stevens Croft | Switch 11 kV CB for site auxiliary transformer
7 |  | Restoration of supply to Annan, Middlebie, Langholm, Newcastelton, Gretna, Lockerbie, Kirkbank and Moffat PS
| 7.1A | Pick up block load at Annan PS | Annan PS | Switch 11 kV CB feeder | [15 empty] | Annan PS | 12.12 |  |  | 81.89% | 12.12
| 7.1B | Control system voltage if necessary | Stevens Croft | Adjust V-setting point for Stevens Croft DER
| 7.1C | Control system frequency if necessary | Stevens Croft | Adjust F-setting point for Stevens Croft DER
| 7.2A | Pick up block load at Middlebie PS | Middlebie PS | Switch 11 kV CB feeder | [15 empty] | Annan PS | 12.12 |  |  | 81.89% | 12.12
| 7.2B | Control system voltage if necessary | Stevens Croft | Adjust V-setting point for Stevens Croft DER
| 7.2C | Control system frequency if necessary | Stevens Croft | Adjust F-setting point for Stevens Croft DER
| 7.3A | Pick up block load at Langholm PS | Langholm PS | Switch 11 kV CB feeder | [15 empty] | Annan PS | 12.12 |  |  | 81.89% | 12.12
| 7.3B | Control system voltage if necessary | Stevens Croft | Adjust V-setting point for Stevens Croft DER
| 7.3C | Control system frequency if necessary | Stevens Croft | Adjust F-setting point for Stevens Croft DER
| 7.4A | Pick up block load at Newcastelton PS | Newcastelton PS | Switch 11 kV CB feeder | [15 empty] | Annan PS | 12.12 |  |  | 81.89% | 12.12
| 7.4B | Control system voltage if necessary | Stevens Croft | Adjust V-setting point for Stevens Croft DER
| 7.4C | Control system frequency if necessary | Stevens Croft | Adjust F-setting point for Stevens Croft DER
| 7.5A | Pick up block load at Gretna PS | Gretna PS | Switch 11 kV CB feeder | [15 empty] | Annan PS | 12.12 |  |  | 81.89% | 12.12
| 7.5B | Control system voltage if necessary | Stevens Croft | Adjust V-setting point for Stevens Croft DER
| 7.5C | Control system frequency if necessary | Stevens Croft | Adjust F-setting point for Stevens Croft DER
| 7.6A | Pick up block load at Gretna PS | Gretna PS | Switch 11 kV CB feeder | [15 empty] | Annan PS | 12.12 |  |  | 81.89%
| 7.6B | Control system voltage if necessary | Stevens Croft | Adjust V-setting point for Stevens Croft DER
| 7.6C | Control system frequency if necessary | Stevens Croft | Adjust F-setting point for Stevens Croft DER
| 7.7A | Pick up block load at Lockerbie PS | Lockerbie PS | Switch 11 kV CB feeder | [15 empty] | Annan PS | 12.12 |  |  | 81.89%
| 7.7B | Control system voltage if necessary | Stevens Croft | Adjust V-setting point for Stevens Croft DER
| 7.7C | Control system frequency if necessary | Stevens Croft | Adjust F-setting point for Stevens Croft DER
| 7.8A | Pick up block load at Moffat PS | Moffat PS | Switch 11 kV CB feeder | [15 empty] | Annan PS | 12.12 |  |  | 81.89%
| 7.8B | Control system voltage if necessary | Stevens Croft | Adjust V-setting point for Stevens Croft DER
| 7.8C | Control system frequency if necessary | Stevens Croft | Adjust F-setting point for Stevens Croft DER
8 |  | Connection of MINSCA WF to Chapelcross GSP network | [7 empty] | 37
| 8.1 | Energise the 33 kV busbar at the WF SPD substation | MINSCA WF (SPD) | Switch 33 kV CB on MINSCA WF side of the circuit | [12 empty] | Chapelcross GSP - MINSCA WF
| 8.2 | Energise the 33 kV busbar at the WF substation (POC) | MINSCA WF (SPD) | Switch 33 kV CB for the circuit to WF POC
| 8.3 | Energise WF transformers and connect MINSCA WF | MINSCA WF | Switch 33 kV CB or CBs to MINSCA WF | [9 empty] | MINSCA WF
| 8.4 | Control system voltage if necessary | MINSCA WF | Adjust V-setting point and control mode for MINSCA WF
| 8.5 | Control system frequency if necessary | MINSCA WF | Adjust F-setting point and control mode for MINSCA WF
9 |  | Connection of EWE HILL WF to Chapelcross GSP network | [7 empty] | 12
| 9.1 | Energise the 33 kV busbar at the WF SPD substation | EWE HILL WF (SPD) | Switch 33 kV CB on EWE HILL WF side of the circuit | [12 empty] | Middlebie SWS - EWE HILL WF
| 9.2 | Energise the 33 kV busbar at the WF substation (POC) | EWE HILL WF (SPD) | Switch 33 kV CB for the circuit to WF POC
| 9.3 | Energise WF transformers and connect EWE HILL WF | EWE HILL WF | Switch 33 kV CB or CBs to EWE HILL WF | [9 empty] | EWE HILL WF
| 9.4 | Control system voltage if necessary | EWE HILL WF | Adjust V-setting point and control mode for EWE HILL WF
| 9.5 | Control system frequency if necessary | EWE HILL WF | Adjust F-setting point and control mode for EWE HILL WF
10 |  | Connection of CRAIG and CRAIG II WF to Chapelcross GSP network | [7 empty] | 10
| 10.1 | Energise the circuit to Craig WF | Langholm PS | Switch 11 kV CB on Langholm PS side of the circuit | [12 empty] | Langholm PS - Craig WF
| 10.2 | Energise the circuit to Craig II WF | Langholm PS | Switch 11 kV CB on Langholm PS side of the circuit | [12 empty] | Langholm PS - Craig II WF
| 10.3 | Energise the 11 kV busbar at Craig WF | Craig WF | Switch 11 kV CB on Craig WF side of the circuit | [12 empty] | Langholm PS - Craig WF
| 10.4 | Energise the 11 kV busbar at Craig II WF | Craig II WF | Switch 11 kV CB on Craig II WF side of the circuit | [12 empty] | Langholm PS - Craig II WF
| 10.5 | Energise WF transformers and connect Craig WF | Craig WF | Switch 11 kV CB or CBs to Craig WF | [9 empty] | Craig WF
| 10.6 | Energise WF transformers and connect Craig II WF | Craig II WF | Switch 11 kV CB or CBs to Craig II WF | [9 empty] | Craig II WF
| 10.7 | Control system voltage if necessary | Craig WF | Adjust V-setting point and control mode for EWE HILL WF
| 10.8 | Control system frequency if necessary | Craig II WF | Adjust F-setting point and control mode for EWE HILL WF

## Option 4 (hidden)
Option 4 – Chapelcross GSP 33 kV Island System to Start Dumfries GSP 33 kV Network
|  | System Restoration Plan | [6 empty] | DER connected |  |  |  |  | Transformers Energised |  |  | Circuits energised |  |  | Block Loads |  |  |  |  | System studies results
Stage | Step | Restoration Description | Locations | Network switching operation and control actions | Description | Sending BB (e.g. CHAP3-) | Receiving BB (e.g. STCR3-) | CB closed (e.g. CHAP3-11) | Name | MVA | MW | kV | Cum. MVA | Name (Substation, Trfr no) | MVA | Inrush Current (Inrush/Irated) | Circuit Name (Source - Destination) | Length (km) | Charging Power (MVAr) | Name | Maximum MVA | Minimum MVA | PF | Maximum % of DER | Load Flow Check | Voltage & Control check | Frequency response check | Transient stability check | System studies results check
1 |  | Energisation of Dumfries GSP
| 1.1 | Energise Carrutherstown second 33 kV busbar and circuit to Dumfries GSP | Carrutherstown | Switch 33 kV CB for Carrutherstown NOP | [6 empty] | 45 | 11 | 45 |  |  |  | Carrutherstown - Dumfries
| 1.2 | Energise Dumfries GSP first 33 kV busbar | Dumfries GSP | Switch 33 kV CB on Dumfries GSP side of the circuit | [12 empty] | Carrutherstown - Dumfries |  |  |  |  | 1.5 | 1
| 1.3 | Energise Dumfries GSP second 33 kV busbar | Dumfries GSP | Switch 33 kV busbar coupler
2 |  | Connection of Dalswinton Wind Farm
| 2.1 | Energize WF transformer and connect Dalswinton WF | Dumfries GSP | Switch 33 kV CB on Dumfries GSP side of the circuit | [10 empty] | 36 |  | Dumfries - Dalswinton WF
| 2.2 | Control system voltage if necessary | Dalswinton WF | Adjust V-setting point and control mode for Dalswinton WF
| 2.3 | Control system frequency if necessary | Dalswinton WF | Adjust F-setting point and control mode for Dalswinton WF
3 |  | Restoration of power supply to Heathall PS and 3 generation sites
| 3.1 | Energise transformer feeder 1 | Dumfries GSP | Switch 33 kV CB to Heathall T1 | [9 empty] | Heathall 33/11 kV T1 | 24 |  | Dumfries - Heathall 1
|  | Energise transformer feeder 2 | Dumfries GSP | [10 empty] | Heathall 33/11 kV T2 | 24 |  | Dumfries - Heathall 2
|  | Pick up block load at Heathall PS automatically | Heathall PS | [16 empty] | Heathall PS | 12.9
| 3.2 | Form double supply loop to Heathall PS | Dumfries GSP | Switch 33 kV CB to Heathall T2
| 3.3 | Control system voltage if necessary | Dalswinton WF | Adjust V-setting point and control mode for Dalswinton WF
| 3.4 | Control system frequency if necessary | Dalswinton WF | Adjust F-setting point and control mode for Dalswinton WF
| 3.5 | Energise and connect Dargavel biomass power plant | Heathall PS | Switch 11 kV CB to Dargavel 11/0.4 kV transformer | [9 empty] | Dargavel 11/0.4 kV | 6.64
| 3.6 | Control system voltage if necessary | Dargavel plant | Adjust V-setting point and control mode for Dargavel unit
| 3.7 | Control system frequency if necessary | Dargavel plant | Adjust F-setting point and control mode for Dargavel unit
| 3.8 | Energise and connect Locharmoss landfill power plant | Heathall PS | Switch 11 kV CB to Locharmoss 11/0.4 kV transformer | [9 empty] | Locharmoss 11/0.4 kV | 0.8
| 3.9 | Control system voltage if necessary | Locharmoss plant | Adjust V-setting point and control mode for Locharmoss unit
| 3.10 | Control system frequency if necessary | Locharmoss plant | Adjust F-setting point and control mode for Locharmoss unit
| 3.11 | Energise and connect Tinwald House Waste incineration plant | Heathall PS | Switch 11 kV CB to Tinwald House 11/0.4 kV transformer | [9 empty] | Tinwald House 11/0.4 kV | ??
| 3.12 | Control system voltage if necessary | Tinwald House plant | Adjust V-setting point and control mode for Tinwald House unit
| 3.13 | Control system frequency if necessary | Tinwald House plant | Adjust F-setting point and control mode for Tinwald House unit
4 |  | Restoration of power supply to Carrutherstown PS
| 4.1 | Energise the circuit to Carrutherstown SWS | Carrutherstown | Switch 33 kV CB on Carrutherstown side of the circuit | [12 empty] | Carrutherstown B - Carrutherstown SWS
| 4.2 | Energise the 33 kV Carrutherstown SWS busbar | Carrutherstown SWS | Switch 33 kV CB on Carrutherstown SWS side of the circuit | [12 empty] | Carrutherstown B - Carrutherstown SWS
| 4.3 | Energise transformer feeder to Carrutherstown PS | Carrutherstown SWS | Switch 33 kV CB to Carrutherstown 33/11 kV transformer | [9 empty] | Carrutherstown 33/11 kV | 7.5
|  | Pick up block load at Carrutherstown PS automatically | Carrutherstown PS | [16 empty] | Carrutherstown PS | 2.2
| 4.4 | Control system voltage if necessary | Dalswinton WF | Adjust V-setting point and control mode for Dalswinton WF
| 4.5 | Control system frequency if necessary | Dalswinton WF | Adjust F-setting point and control mode for Dalswinton WF
| 4.6 | Energise the second circuit to Carrutherstown 33 kV | Carrutherstown SWS | Switch 33 kV CB on Carrutherstown SWS side of the circuit | [12 empty] | Carrutherstown A - Carrutherstown SWS
5 |  | Restoration of power supply to Cargenbridge PS
| 5.1 | Energise transformer feeder 1 | Dumfries GSP | Switch 33 kV CB to Cargenbridge T1 | [9 empty] | Cargenbridge 33/11 kV T1 | 21 |  | Dumfries - Cargenbridge 1
|  | Energise transformer feeder 2 | Dumfries GSP | [10 empty] | Cargenbridge 33/11 kV T2 | 21 |  | Dumfries - Cargenbridge 2
|  | Pick up block load at Cargenbridge PS automatically | Cargenbridge PS | [16 empty] | Cargenbridge PS | 7.23
| 5.2 | Form double supply loop to Cargenbridge PS | Dumfries GSP | Switch 33 kV CB to Cargenbridge T2
| 5.3 | Control system voltage if necessary | Dalswinton WF | Adjust V-setting point and control mode for Dalswinton WF
| 5.4 | Control system frequency if necessary | Dalswinton WF | Adjust F-setting point and control mode for Dalswinton WF
6 |  | Restoration of power supply to Maxwellton and Stelrad PS
| 6.1 | Energise transformer feeder to Maxwellton T1 | Dumfries GSP | Switch 33 kV CB to Maxwellton T1 and Stelrad | [9 empty] | Maxwellton 33/11 kV T1 | 24 |  | Dumfries - Maxwellton T1
|  | Energise transformer feeder to Maxwellton T2 | Dumfries GSP | [10 empty] | Maxwellton 33/11 kV T2 | 24 |  | Dumfries - Maxwellton T2
|  | Energise transformer feeder to Stelrad T1 | Dumfries GSP | [10 empty] | Stelrad 33/11 kV T1 | 24 |  | Dumfries - Stelrad
|  | Pick up block load at Maxwellton PS automatically | Maxwellton PS | [16 empty] | Maxwellton PS | 12.94
|  | Pick up block load at Stelrad PS automatically | Stelrad PS | [16 empty] | Stelrad PS | 2
| 6.2 | Form double supply loop to Maxwellton | Dumfries GSP | Switch 33 kV CB to Maxwellton T2
| 6.3 | Control system voltage if necessary | Dalswinton WF | Adjust V-setting point and control mode for Dalswinton WF
| 6.4 | Control system frequency if necessary | Dalswinton WF | Adjust F-setting point and control mode for Dalswinton WF
7 |  | Restoration of power supply to Lochside and Dunscore PS
| 7.1 | Energise transformer feeder to Lochside T1 | Dumfries GSP | Switch 33 kV CB to Lochside | [9 empty] | Lochside 33/11 kV T1 | 10 |  | Dumfries - Penpont A
|  | Pick up block load at Lochside PS automatically | Lochside PS | [16 empty] | Lochside PS | 2.55
|  | Energise transformer feeder to Dunscore T1 | Dumfries GSP | [10 empty] | Dunscore 33/11 kV T1 | 7.5 |  | Dumfries - Penpont A
|  | Pick up block load at Dunscore PS automatically | Dunscore PS | [16 empty] | Dunscore PS | 1.2
| 7.2 | Control system voltage if necessary | Dalswinton WF | Adjust V-setting point and control mode for Dalswinton WF
| 7.3 | Control system frequency if necessary | Dalswinton WF | Adjust F-setting point and control mode for Dalswinton WF
8 |  | Restoration of power supply to Penpont PS
| 8.1 | Energise the first 33 kV busbar at Penpoint A | Penpont A | Switch 33 kV CB on Penpont A side of the circuit | [12 empty] | Dumfries - Penpont A
| 8.2 | Energise the circuit to Penpont B | Dumfries GSP | Switch 33 kV CB on Dumfries side of the circuit | [12 empty] | Dumfries - Penpont B
| 8.3 | Energise the second 33 kV busbar at Penpoint B | Penpont B | Switch 33 kV CB on Penpont B side of the circuit | [12 empty] | Dumfries - Penpont B
| 8.4 | Energise transformer feeder 1 to Penpoint PS T1 | Penpont A | Switch 33 kV CB to Penpont 33/11 kV T1 | [9 empty] | Penpont 33/11 kV T1 | 10
|  | Energise transformer feeder 2 to Penpont PS T2 | Penpont A | [10 empty] | Penpont 33/11 kV T2 | 10
|  | Pick up block load at Penpont PS automatically | Penpont B | [16 empty] | Penpont PS | 4.62
| 8.5 | Form double supply loop to Penpoint PS | Penpont B | Switch 33 kV CB to Penpont 33/11 kV T2
| 8.5 | Energize WF transformer and connect Wetherhill WF | Penpont B | Switch 33 kV CB on Penpont B side of the circuit | [9 empty] | Wetherhill T1 | 19.9 |  | Penpont B - Wetherhill WF
| 8.7 | Control system voltage if necessary | Dalswinton WF | Adjust V-setting point and control mode for Dalswinton WF
| 8.8 | Control system frequency if necessary | Dalswinton WF | Adjust F-setting point and control mode for Dalswinton WF

## Option 5 (hidden)
Option 5 – Chapelcross GSP 33 kV Island System to Start Dumfries GSP 132/33 kV Network
|  | System Restoration Plan | [6 empty] | DER connected |  |  |  |  | Transformers Energised |  |  | Circuits energised |  |  | Block Loads |  |  |  |  | System studies results
Stage | Step | Restoration Description | Locations | Network switching operation and control actions | Description | Sending BB (e.g. CHAP3-) | Receiving BB (e.g. STCR3-) | CB closed (e.g. CHAP3-11) | Name | MVA | MW | kV | Cum. MVA | Name (Substation, Trfr no) | MVA | Inrush Current (Inrush/Irated) | Circuit Name (Source - Destination) | Length (km) | Charging Power (MVAr) | Name | Maximum MVA | Minimum MVA | PF | Maximum % of DER | Load Flow Check | Voltage & Control check | Frequency response check | Transient stability check | System studies results check
1 |  | Restoration of Chapelcross 132 kV network
| 1.1 | Energise Chapelcross 132/33 kV GT1 | Chapelcross GSP | Switch 33 kV CB for 132/33 kV GT1 | [9 empty] | 132/33 kV Chapelcross GT1 | 90
| 1.2 | Energise Chapelcross 132 kV busbar | Chapelcross GSP | Switch 132 kV CB for 132/33 kV GT1 | [9 empty] | 132/33 kV Chapelcross GT1 | 90
| 1.3 | Energise Chapelcross 132/33 kV GT2 | Chapelcross GSP | Switch 132 kV CB for 132/33 kV GT2 | [9 empty] | 132/33 kV Chapelcross GT2 | 90
| 1.4 | Operate Chapelcross 132/33 kV GT1 and GT2 in parallel | Chapelcross GSP | Switch 33 kV CB for 132/33 kV GT2 | [9 empty] | 132/33 kV Chapelcross GT2 | 90
| 1.5 | Change tap positions of the two GTs to maintain voltage profile at 132 kV within acceptable limits. | Chapelcross GSP
2 |  | Connection of Dumfries 132 kV
| 2.1 | Energise the circuit to Dumfries GSP | Chapelcross GSP | Switch 132 kV CB at Chapelcross GSP | [12 empty] | Chapelcross 132 kV - Dumfries 132 kV
| 2.2 | Energise Dumfries GSP busbar | Dumfries GSP | Switch 132 kV CB at Dumfries GSP | [12 empty] | Chapelcross 132 kV - Dumfries 132 kV
| 2.3 | Energise the second circuit to Dumfries GSP | Chapelcross GSP | Switch 132 kV CB at Chapelcross GSP | [12 empty] | Chapelcross 132 kV - Dumfries 132 kV
| 2.4 | Operate Chapelcross 132 kV circuits 1 and 2 in parallel | Dumfries GSP | Switch 132 kV CB at Dumfries GSP | [12 empty] | Chapelcross 132 kV - Dumfries 132 kV
3 |  | Energisation of Dumfries GSP
| 3.1 | Energise Dumfries GSP GT1 | Dumfries GSP | Switch 132 kV CB at Dumfries GSP | [6 empty] | 45 | 11 | 45 | 132/33 kV Dumfries GT1 | 90
| 3.2 | Energise Dumfries GSP first 33 kV busbar | Dumfries GSP | Switch 33 kV CB at Dumfries GSP | [9 empty] | 132/33 kV Dumfries GT1 | 90 | [6 empty] | 1.5 | 1
| 3.3 | Energise Dumfries GSP second 33 kV busbar | Dumfries GSP | Switch 33 kV busbar coupler
| 3.4 | Energise Dumfries 132/33 kV GT2 | Dumfries GSP | Switch 132 kV CB for 132/33 kV GT2 | [9 empty] | 132/33 kV Dumfries GT2 | 90
| 3.5 | Operate Dumfries 132/33 kV GT1 and GT2 in parallel | Dumfries GSP | Switch 33 kV CB for 132/33 kV GT2 | [9 empty] | 132/33 kV Dumfries GT2 | 90
4 |  | Connection of Dalswinton Wind Farm
| 4.1 | Energize WF transformer and connect Dalswinton WF | Dumfries GSP | Switch 33 kV CB on Dumfries GSP side of the circuit | [10 empty] | 36 |  | Dumfries - Dalswinton WF
| 4.2 | Control system voltage if necessary | Dalswinton WF | Adjust V-setting point and control mode for Dalswinton WF
| 4.3 | Control system frequency if necessary | Dalswinton WF | Adjust F-setting point and control mode for Dalswinton WF
5 |  | Restoration of power supply to Heathall PS and 3 generation sites
| 5.1 | Energise transformer feeder 1 | Dumfries GSP | Switch 33 kV CB to Heathall T1 | [9 empty] | Heathall 33/11 kV T1 | 24 |  | Dumfries - Heathall 1
|  | Energise transformer feeder 2 | Dumfries GSP | [10 empty] | Heathall 33/11 kV T2 | 24 |  | Dumfries - Heathall 2
|  | Pick up block load at Heathall PS automatically | Heathall PS | [16 empty] | Heathall PS | 12.9
| 5.2 | Form double supply loop to Heathall PS | Dumfries GSP | Switch 33 kV CB to Heathall T2
| 5.3 | Control system voltage if necessary | Dalswinton WF | Adjust V-setting point and control mode for Dalswinton WF
| 5.4 | Control system frequency if necessary | Dalswinton WF | Adjust F-setting point and control mode for Dalswinton WF
| 5.5 | Energise and connect Dargavel biomass power plant | Heathall PS | Switch 11 kV CB to Dargavel 11/0.4 kV transformer | [9 empty] | Dargavel 11/0.4 kV | 6.64
| 5.6 | Control system voltage if necessary | Dargavel plant | Adjust V-setting point and control mode for Dargavel unit
| 5.7 | Control system frequency if necessary | Dargavel plant | Adjust F-setting point and control mode for Dargavel unit
| 5.8 | Energise and connect Locharmoss landfill power plant | Heathall PS | Switch 11 kV CB to Locharmoss 11/0.4 kV transformer | [9 empty] | Locharmoss 11/0.4 kV | 0.8
| 5.9 | Control system voltage if necessary | Locharmoss plant | Adjust V-setting point and control mode for Locharmoss unit
| 5.1 | Control system frequency if necessary | Locharmoss plant | Adjust F-setting point and control mode for Locharmoss unit
| 5.11 | Energise and connect Tinwald House Waste incineration plant | Heathall PS | Switch 11 kV CB to Tinwald House 11/0.4 kV transformer | [9 empty] | Tinwald House 11/0.4 kV | ??
| 5.12 | Control system voltage if necessary | Tinwald House plant | Adjust V-setting point and control mode for Tinwald House unit
| 5.13 | Control system frequency if necessary | Tinwald House plant | Adjust F-setting point and control mode for Tinwald House unit
6 |  | Restoration of power supply to Carrutherstown PS
| 6.1 | Energise the circuit to Carrutherstown SWS | Carrutherstown | Switch 33 kV CB on Carrutherstown side of the circuit | [12 empty] | Carrutherstown B - Carrutherstown SWS
| 6.2 | Energise the 33 kV Carrutherstown SWS busbar | Carrutherstown SWS | Switch 33 kV CB on Carrutherstown SWS side of the circuit | [12 empty] | Carrutherstown B - Carrutherstown SWS
| 6.3 | Energise transformer feeder to Carrutherstown PS | Carrutherstown SWS | Switch 33 kV CB to Carrutherstown 33/11 kV transformer | [9 empty] | Carrutherstown 33/11 kV T1 | 7.5
|  | Pick up block load at Carrutherstown PS automatically | Carrutherstown PS | [16 empty] | Carrutherstown PS | 2.2
| 6.4 | Control system voltage if necessary | Dalswinton WF | Adjust V-setting point and control mode for Dalswinton WF
| 6.5 | Control system frequency if necessary | Dalswinton WF | Adjust F-setting point and control mode for Dalswinton WF
| 6.6 | Energise the second circuit to Carrutherstown 33 kV | Carrutherstown SWS | Switch 33 kV CB on Carrutherstown SWS side of the circuit | [12 empty] | Carrutherstown A - Carrutherstown SWS
7 |  | Restoration of power supply to Cargenbridge PS
| 7.1 | Energise transformer feeder 1 | Dumfries GSP | Switch 33 kV CB to Cargenbridge T1 | [9 empty] | Cargenbridge 33/11 kV T1 | 21 |  | Dumfries - Cargenbridge 1
|  | Energise transformer feeder 2 | Dumfries GSP | [10 empty] | Cargenbridge 33/11 kV T2 | 21 |  | Dumfries - Cargenbridge 2
|  | Pick up block load at Cargenbridge PS automatically | Cargenbridge PS | [16 empty] | Cargenbridge PS | 7.23
| 7.2 | Form double supply loop to Cargenbridge PS | Dumfries GSP | Switch 33 kV CB to Cargenbridge T2
| 7.3 | Control system voltage if necessary | Dalswinton WF | Adjust V-setting point and control mode for Dalswinton WF
| 7.4 | Control system frequency if necessary | Dalswinton WF | Adjust F-setting point and control mode for Dalswinton WF
8 |  | Restoration of power supply to Maxwellton and Stelrad PS
| 8.1 | Energise transformer feeder to Maxwellton T1 | Dumfries GSP | Switch 33 kV CB to Maxwellton T1 and Stelrad | [9 empty] | Maxwellton 33/11 kV T1 | 24 |  | Dumfries - Maxwellton T1
|  | Energise transformer feeder to Maxwellton T2 | Dumfries GSP | [10 empty] | Maxwellton 33/11 kV T2 | 24 |  | Dumfries - Maxwellton T2
|  | Energise transformer feeder to Stelrad T1 | Dumfries GSP | [10 empty] | Stelrad 33/11 kV T1 | 24 |  | Dumfries - Stelrad
|  | Pick up block load at Maxwellton PS automatically | Maxwellton PS | [16 empty] | Maxwellton PS | 12.94
|  | Pick up block load at Stelrad PS automatically | Stelrad PS | [16 empty] | Stelrad PS | 2
| 8.2 | Form double supply loop to Maxwellton | Dumfries GSP | Switch 33 kV CB to Maxwellton T2
| 8.3 | Control system voltage if necessary | Dalswinton WF | Adjust V-setting point and control mode for Dalswinton WF
| 8.4 | Control system frequency if necessary | Dalswinton WF | Adjust F-setting point and control mode for Dalswinton WF
9 |  | Restoration of power supply to Lochside and Dunscore PS
| 9.1 | Energise transformer feeder to Lochside T1 | Dumfries GSP | Switch 33 kV CB to Lochside | [9 empty] | Lochside 33/11 kV T1 | 10 |  | Dumfries - Penpont A
|  | Pick up block load at Lochside PS automatically | Lochside PS | [16 empty] | Lochside PS | 2.55
|  | Energise transformer feeder to Dunscore T1 | Dumfries GSP | [10 empty] | Dunscore 33/11 kV T1 | 7.5 |  | Dumfries - Penpont A
|  | Pick up block load at Dunscore PS automatically | Dunscore PS | [16 empty] | Dunscore PS | 1.2 |  |  |  | 1.2
| 9.2 | Control system voltage if necessary | Dalswinton WF | Adjust V-setting point and control mode for Dalswinton WF
| 9.3 | Control system frequency if necessary | Dalswinton WF | Adjust F-setting point and control mode for Dalswinton WF
10 |  | Restoration of power supply to Penpont PS
| 10.1 | Energise the first 33 kV busbar at Penpoint A | Penpont A | Switch 33 kV CB on Penpont A side of the circuit | [12 empty] | Dumfries - Penpont A
| 10.2 | Energise the circuit to Penpont B | Dumfries GSP | Switch 33 kV CB on Dumfries side of the circuit | [12 empty] | Dumfries - Penpont B
| 10.3 | Energise the second 33 kV busbar at Penpoint B | Penpont B | Switch 33 kV CB on Penpont B side of the circuit | [12 empty] | Dumfries - Penpont B
| 10.4 | Energise transformer feeder 1 to Penpoint PS T1 | Penpont A | Switch 33 kV CB to Penpont 33/11 kV T1 | [9 empty] | Penpont 33/11 kV T1 | 10
|  | Energise transformer feeder 2 to Penpont PS T2 | Penpont A | [10 empty] | Penpont 33/11 kV T2 | 10
|  | Pick up block load at Penpont PS automatically | Penpont B | [16 empty] | Penpont PS | 4.62 |  |  |  | 4.62
| 10.5 | Form double supply loop to Penpoint PS | Penpont B | Switch 33 kV CB to Penpont 33/11 kV T2
| 10.5 | Energize WF transformer and connect Wetherhill WF | Penpont B | Switch 33 kV CB on Penpont B side of the circuit | [9 empty] | Wetherhill T1 | 19.9 |  | Penpont B - Wetherhill WF
| 10.7 | Control system voltage if necessary | Dalswinton WF | Adjust V-setting point and control mode for Dalswinton WF
| 10.8 | Control system frequency if necessary | Dalswinton WF | Adjust F-setting point and control mode for Dalswinton WF

## Option 6 (hidden)
Option 6 – Chapelcross GSP 33 kV Island System to Start Gretna 400 kV Network
|  | System Restoration Plan | [6 empty] | DER connected |  |  |  |  | Transformers Energised |  |  | Circuits energised |  |  | Block Loads |  |  |  |  | System studies results
Stage | Step | Restoration Description | Locations | Network switching operation and control actions | Description | Sending BB (e.g. CHAP3-) | Receiving BB (e.g. STCR3-) | CB closed (e.g. CHAP3-11) | Name | MVA | MW | kV | Cum. MVA | Name (Substation, Trfr no) | MVA | Inrush Current (Inrush/Irated) | Circuit Name (Source - Destination) | Length (km) | Charging Power (MVAr) | Name | Maximum MVA | Minimum MVA | PF | Maximum % of DER | Load Flow Check | Voltage & Control check | Frequency response check | Transient stability check | System studies results check
1 |  | Restoration of Chapelcross 132 kV network
| 1.1 | Energise Chapelcross 132/33 kV GT1 | Chapelcross GSP | Switch 33 kV CB for 132/33 kV GT1 | [9 empty] | 132/33 kV Chapelcross GT1
| 1.2 | Energise Chapelcross 132 kV busbar | Chapelcross GSP | Switch 132 kV CB for 132/33 kV GT1 | [9 empty] | 132/33 kV Chapelcross GT1
| 1.3 | Energise Chapelcross 132/33 kV GT2 | Chapelcross GSP | Switch 132 kV CB for 132/33 kV GT2 | [9 empty] | 132/33 kV Chapelcross GT2
| 1.4 | Operate Chapelcross 132/33 kV GT1 and GT2 in parallel | Chapelcross GSP | Switch 33 kV CB for 132/33 kV GT2 | [9 empty] | 132/33 kV Chapelcross GT2
| 1.5 | Change tap positions of the two GTs to maintain voltage profile at 132 kV within acceptable limits. | Chapelcross GSP
2 |  | Connection of Dumfries 132 kV
| 2.1 | Energise the first circuit to Gretna GSP | Chapelcross GSP | Switch 132 kV CB at Chapelcross GSP side of the circuit | [12 empty] | Chapelcross 132 kV - Gretna 132 kV 1
| 2.2 | Energise Gretna GSP busbar | Gretna GSP | Switch 132 kV CB at Gretna GSP side of the circuit | [12 empty] | Chapelcross 132 kV - Gretna 132 kV 1
| 2.3 | Energise the second circuit to Gretna GSP | Chapelcross GSP | Switch 132 kV CB at Chapelcross GSP side of the circuit | [12 empty] | Chapelcross 132 kV - Gretna 132 kV 2
| 2.4 | Operate Chapelcross 132 kV circuits 1 and 2 in parallel | Gretna GSP | Switch 132 kV CB at Gretna GSP side of the circuit | [12 empty] | Chapelcross 132 kV - Gretna 132 kV 2
3 |  | Connection of Gretna 132 kV Wind Farm
| 3.1 | Energize WF transformer and connect Gretna WF | Gretna GSP | Switch 132 kV CB to transformer feeder of 132 kV connected Wind Farm | [12 empty] | Gretna GSP - Gretna WF
| 3.2 | Control system voltage if necessary | Gretna WF | Adjust V-setting point and control mode for Gretna WF
| 3.3 | Control system frequency if necessary | Gretna WF | Adjust F-setting point and control mode for Gretna WF
4 |  | Connection of NGET 400 kV network at Gretna GSP
| 4.1 | Energise Gretna 400/132 kV SGT1 | Gretna GSP | Switch 132 kV CB for 400/132 kV SGT1 | [9 empty] | 400/132 kV Gretna SGT1
| 4.2 | Energise Gretna 400 kV busbar | Gretna GSP | Switch 400 kV CB for 400/132 kV SGT1 | [9 empty] | 400/132 kV Gretna SGT1
| 4.3 | Energise Gretna 400/132 kV SGT2 | Gretna GSP | Switch 400 kV CB for 400/132 kV SGT2 | [9 empty] | 400/132 kV Gretna SGT2
| 4.4 | Operate Gretna 400/132 kV GT1 and GT2 in parallel | Gretna GSP | Switch 132 kV CB for 400/132 kV SGT2 | [9 empty] | 400/132 kV Gretna SGT2
| 4.5 | Change tap positions of the two SGTs to maintain voltage profile at 400 kV within acceptable limits. | Gretna GSP
| 4.6 | Energise 400 kV circuit to Harker including the series capacitor compensation | Gretna GSP | Switch 400 kV CB's at Gretna GSP | [12 empty] | Gretna 400 kV - Harker 400 kV