## Generators - Active Power
Generators - Active Power
Results
Lines
[6 empty] | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[6 empty] | Active Power >>> |  | 4.512 | 4.512 | 4.512 | 5.0106 | 5.0106 | 5.514 | 5.514 | 5.5491 | 5.5491 | 5.5491 | 5.6469 | 5.6469 | 5.6469 | 5.6469 | 5.6469 | 15.9019 | 26.1569 | 30.8845 | 37.5336 | 45.2146 | 39.3507 | 39.3507 | 66.8135 | 66.8135 | 66.8135 | 66.8135 | 58.1976 | 61.0638 | 55.9128 | 55.9128 | 55.9128 | 55.9128 | 55.9128 | 33 | 34
|  |  | Name | Min P | Max P | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  | STCR5-_1 | 0 | 45 | 0 | 0 | 4.512 | 4.512 | 4.512 | 5.0106 | 5.0106 | 5.514 | 5.514 | 5.5491 | 5.5491 | 5.5491 | 5.6469 | 5.6469 | 5.6469 | 5.6469 | 5.6469 | 15.9019 | 26.1569 | 30.8845 | 19.7336 | 27.4146 | 21.5507 | 21.5507 | 44.5635 | 44.5635 | 34.5635 | 34.5635 | 25.9476 | 28.8138 | 23.6628 | 23.6628 | 23.6628 | 23.6628 | 23.6628 | 23.6628 | 23.6628 | 4.5 | 4.512 | 4.512 | 5.0106 | 5.514 | 5.5491 | 5.6469 | 26.1569 | 30.8845 | 17.5336 | 25.2146 | 19.3506 | 41.8135 | 33.1976 | 36.0638 | 30.9127
|  |  | CRAG0A_1 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | CRAG0B_1 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10
|  |  | EWHC0G_1 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 2.4 | 2.4 | 2.4 | 3 | 3 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 5
|  |  | WYSB0G_1 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MINS0G_1 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6 | 7.6 | 7.6 | 7.6 | 9.5 | 9.5 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  | WTG_EWEH0G_1 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8 | 7.8 | 7.8 | 7.8 | 9.75 | 9.75 | 9.75 | 9.75 | 9.75 | 9.75 | 9.75 | 9.75 | 9.75 | 9.75 | 9.75 | 9.75 | 9.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | STCR_D1 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | STCR_MOTOR | 999 | 999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
End Of Sheet
[8 empty] | 4.512 | 4.512 | 4.512 | 5.0106 | 5.0106 | 5.514 | 5.514 | 5.5491 | 5.5491 | 5.5491 | 5.6469 | 5.6469 | 5.6469 | 5.6469 |  | 26.1569 | 26.1569 | 30.8845 | 37.5336 | 45.2146 | 39.3507 | 39.3507 | 66.8135 | 66.8135 | 66.8135 | 66.8135 | 58.1976 | 61.0638 | 55.9128 | 55.9128 | 55.9128 | 55.9128 | 55.9128 | 55.9128 | 55.9128
Vlookup
Note on Z9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cells in yellow are manually calculated to match switching steps. Current flow won't match.

## Generators - Reactive Power
Generators - Reactive Power
Results
Lines
[6 empty] | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[6 empty] | Reactive Power >>> | [36 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  | Name | Min Q | Max Q | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  | STCR5-_1 | -18.6347 | 18.6347 | 0 | 0 | 0.914 | -4.2712 | -4.2712 | -3.5395 | -3.5395 | -3.8689 | -3.8689 | -4.8861 | -4.8861 | -4.8861 | -5.8352 | -5.8352 | -5.8352 | -5.8352 | -5.8352 | -1.0101 | -1.0101 | -0.50482 | -0.50482 | -3.203 | -3.616 | -5.2192 | -5.2192 | -2.5609 | -2.5609 | -2.5609 | -5.4741 | -5.0904 | -5.9665 | -5.9665 | -5.9665 | -5.9665 | -5.9665 | -5.9665 | -5.9665 | 0.914 | -4.2712 | -4.2712 | -3.5395 | -3.8689 | -4.8861 | -5.8352 | -1.0101 | -0.50482 | -3.203 | -3.616 | -5.2192 | -2.5609 | -5.4741 | -5.0904 | -5.9665
|  |  | CRAG0A_1 | -3.4697 | 3.4697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | CRAG0B_1 | -0.78137 | 0.78137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2925e-26 | -1.2925e-26 | 6.4623e-27 | 6.4623e-27 | -1.2925e-26 | -1.2925e-26 | -1.2925e-26 | 6.4623e-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2925e-26 | -1.2925e-26 | 6.4623e-27 | -1.2925e-26 | 6.4623e-27 | 0 | 0
|  |  | EWHC0G_1 | -3.944 | 3.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.944 | 3.944 | 3.944 | 3.4283 | 3.7246 | 2.6496 | 2.6496 | 2.6496 | 2.6496 | 2.6496 | 2.6496 | 2.6496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.944 | 3.4283 | 3.7246 | 2.6496
|  |  | WYSB0G_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MINS0G_1 | -10.49 | 14.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8305 | 6.5513 | 3.1258 | 3.1258 | 9.7571 | 9.7571 | 9.7571 | 4.7087 | 5.5466 | 3.7187 | 3.7187 | 3.7187 | 3.7187 | 3.7187 | 3.7187 | 3.7187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8305 | 6.5513 | 3.1258 | 9.7571 | 4.7087 | 5.5466 | 3.7187
|  |  | WTG_EWEH0G_1 | -10.92 | 15.6422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | STCR_D1 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | STCR_MOTOR | 999 | 999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
End Of Sheet
Vlookup
Note on AD9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cells in yellow: Values are not correct, powerflow needs to be rerun.

## Generators - Rating
Generators - Rating
Results
Lines
|  |  |  | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
|  |  |  | Reactive Power >>> | [36 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  | Name | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  | STCR5-_1 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 0.914 | -4.2712 | -4.2712 | -3.5395 | -3.8689 | -4.8861 | -5.8352 | -1.0101 | -0.50482 | -3.203 | -3.616 | -5.2192 | -2.5609 | -5.4741 | -5.0904 | -5.9665
|  |  | CRAG0A_1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | CRAG0B_1 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2925e-26 | -1.2925e-26 | 6.4623e-27 | -1.2925e-26 | 6.4623e-27 | 0 | 0
|  |  | EWHC0G_1 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.944 | 3.4283 | 3.7246 | 2.6496
|  |  | WYSB0G_1 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MINS0G_1 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8305 | 6.5513 | 3.1258 | 9.7571 | 4.7087 | 5.5466 | 3.7187
|  |  | WTG_EWEH0G_1 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | STCR_D1 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | STCR_MOTOR | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
End Of Sheet
Vlookup

## Busbars - Voltage(pu)
Busbars - Voltage(pu)
Results
Lines
|  |  |  | Name in Simulation SLD | PowerFactory names |  | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[7 empty] | Magnitude (pu) >>> | V should be > 0 | [35 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  |  | Name |  | Nom Volt (kV) | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  |  | ECCF1K | ECCF1K | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | CHAP1A- | CHAP1A- | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0061 | 1.0061 | 1.0061 | 1.0123 | 1.0123 | 1.0123 | 1.0123 | 1.0123 | 0.78984 | 0.78984 | 0.78672 | 0.78672 | 0.78672 | 0.79908 | 0.99367 | 0.99367 | 0.79186 | 0.79186 | 0.79186 | 0.98928 | 0.80134 | 0.99203 | 0.99203 | 0.99203 | 0.99203 | 0.99203 | 0.99203 | 0.99203 | [5 empty] | 1.0061 | 1.0123 | 0.78984 | 0.78672 | 0.78672 | 0.79908 | 0.99367 | 0.79186 | 0.98928 | 0.80134 | 0.99203
|  |  |  | Terminal | Terminal | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | HAKB1- | HAKB1- | 132 | 0 | 0 | 1.0394 | 1.0394 | 1.0394 | 1.0394 | 1.0394 | 1.0394 | 1.0394 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.0394 | 1.0394 | 1.0394 | 1.0394 | 1.0394 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151
|  |  |  | Terminal(1) | Terminal(1) | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chapelcross 132kV BB |  |  | Y | CHAP1- | CHAP1- | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0061 | 1.0061 | 1.0061 | 1.0123 | 1.0123 | 1.0123 | 1.0123 | 1.0123 | 0.78984 | 0.78984 | 0.78672 | 0.78672 | 0.78672 | 0.79908 | 0.99367 | 0.99367 | 0.79186 | 0.79186 | 0.79186 | 0.98928 | 0.80134 | 0.99203 | 0.99203 | 0.99203 | 0.99203 | 0.99203 | 0.99203 | 0.99203 | 0 | 0 | 0 | 0 | 0 | 1.0061 | 1.0123 | 0.78984 | 0.78672 | 0.78672 | 0.79908 | 0.99367 | 0.79186 | 0.98928 | 0.80134 | 0.99203
|  |  |  | ECCF1J | ECCF1J | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gretna 132kV |  |  | Y | GRNA1- | GRNA1- | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0128 | 1.0128 | 1.0128 | 1.0128 | 1.0128 | 0.79021 | 0.79021 | 0.78709 | 0.78709 | 0.78709 | 0.79945 | 0.99414 | 0.99414 | 0.79224 | 0.79224 | 0.79224 | 0.98975 | 0.80172 | 0.9925 | 0.9925 | 0.9925 | 0.9925 | 0.9925 | 0.9925 | 0.9925 | 1.019 | 1.019 | 1.019 | 1.019 | 1.019 | 0 | 1.0128 | 0.79021 | 0.78709 | 0.78709 | 0.79945 | 0.99414 | 0.79224 | 0.98975 | 0.80172 | 0.9925
|  |  |  | DUMF1- | DUMF1- | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Langholm 33/11kV T1 |  |  |  | LAHOT1 | LAHOT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86427 | 0.92415 | 0.92415 | 0.92114 | 0.92114 | 0.92114 | 0.9353 | 0.93343 | 0.96081 | 0.96081 | 0.96081 | 0.96081 | 0.96081 | 0.96081 | 0.96081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86427 | 0.92415 | 0.92114 | 0.9353 | 0.93343 | 0.96081
Middlebie 33kV BB |  |  |  | MIBI3- | MIBI3- | 33 | 0 | 0 | 0 | 0 | 1.0162 | 1.0162 | 1.0162 | 1.0162 | 1.0162 | 1.0205 | 1.0205 | 1.0205 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 0.98416 | 0.98416 | 0.96473 | 0.96473 | 0.96473 | 0.96755 | 0.98635 | 0.98635 | 0.98357 | 0.98357 | 0.98357 | 0.99676 | 0.99503 | 1.0013 | 1.0013 | 1.0013 | 1.0013 | 1.0013 | 1.0013 | 1.0013 | 0 | 0 | 0 | 0 | 1.0162 | 1.0205 | 1.0244 | 0.98416 | 0.96473 | 0.96473 | 0.96755 | 0.98635 | 0.98357 | 0.99676 | 0.99503 | 1.0013
|  |  |  | CHAPX3 | CHAPX3 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99885 | 0.99885 | 0.98468 | 0.98468 | 0.98468 | 0.99893 | 0.99657 | 0.9897 | 0.9897 | 0.9897 | 0.9897 | 0.9897 | 0.9897 | 0.9897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99885 | 0.98468 | 0.99893 | 0.99657 | 0.9897
Lockerbie 33kV BB A |  |  |  | LOBI3A | LOBI3A | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92033 | 0.92033 | 0.92033 | 0.94507 | 0.952 | 0.97311 | 0.97311 | 0.97311 | 0.97311 | 0.97311 | 0.97311 | 0.97311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92033 | 0.94507 | 0.952 | 0.97311
Moffat 33/11kV T2 |  |  |  | MOFTT2 | MOFTT2 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8942 | 0.93489 | 0.93489 | 0.93489 | 0.93489 | 0.93489 | 0.93489 | 0.93489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8942 | 0.93489
Langholm 33kV BB A |  |  |  | LAHO3A | LAHO3A | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86427 | 0.86427 | 0.92415 | 0.92415 | 0.92114 | 0.92114 | 0.92114 | 0.9353 | 0.93343 | 0.96081 | 0.96081 | 0.96081 | 0.96081 | 0.96081 | 0.96081 | 0.96081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86427 | 0.92415 | 0.92114 | 0.9353 | 0.93343 | 0.96081
Newcastleton 33/11kV T1 |  |  |  | NEWCT1 | NEWCT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98887 | 0.98887 | 0.97997 | 0.97997 | 0.97997 | 0.9943 | 0.99192 | 0.98296 | 0.98296 | 0.98296 | 0.98296 | 0.98296 | 0.98296 | 0.98296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98887 | 0.97997 | 0.9943 | 0.99192 | 0.98296
|  |  |  | CHAPX4 | CHAPX4 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90401 | 0.92286 | 0.95516 | 0.95516 | 0.95516 | 0.95516 | 0.95516 | 0.95516 | 0.95516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90401 | 0.92286 | 0.95516
Langholm 33/11kV T2 |  |  |  | LAHOT2 | LAHOT2 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99552 | 0.99552 | 0.98315 | 0.98315 | 0.98315 | 0.99743 | 0.99506 | 0.98614 | 0.98614 | 0.98614 | 0.98614 | 0.98614 | 0.98614 | 0.98614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99552 | 0.98315 | 0.99743 | 0.99506 | 0.98614
Annan 33/11kV T1 |  |  |  | ANANT1 | ANANT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97736 | 0.97736 | 0.97549 | 0.97549 | 0.97549 | 0.99276 | 1.0024 | 1.0024 | 0.98374 | 0.98374 | 0.98374 | 0.99794 | 0.99558 | 1.0007 | 1.0007 | 1.0007 | 1.0007 | 1.0007 | 1.0007 | 1.0007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97736 | 0.97549 | 0.97549 | 0.99276 | 1.0024 | 0.98374 | 0.99794 | 0.99558 | 1.0007
Chapelcross 33kV BB |  |  |  | CHAP3- | CHAP3- | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gretna 33/11 kV T1 |  |  |  | GRNAT1 | GRNAT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99937 | 0.99937 | 0.98519 | 0.98519 | 0.98519 | 0.99945 | 0.99709 | 0.98625 | 0.98625 | 0.98625 | 0.98625 | 0.98625 | 0.98625 | 0.98625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99937 | 0.98519 | 0.99945 | 0.99709 | 0.98625
|  |  |  | CHAPX1 | CHAPX1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98249 | 0.98249 | 0.98249 | 0.99729 | 0.99556 | 1.0017 | 1.0017 | 1.0017 | 1.0017 | 1.0017 | 1.0017 | 1.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98249 | 0.99729 | 0.99556 | 1.0017
|  |  |  | WYSB3- | WYSB3- | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gretna 33kV BB A |  |  |  | GRNA3A | GRNA3A | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99937 | 0.99937 | 0.98519 | 0.98519 | 0.98519 | 0.99945 | 0.99709 | 0.98625 | 0.98625 | 0.98625 | 0.98625 | 0.98625 | 0.98625 | 0.98625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99937 | 0.98519 | 0.99945 | 0.99709 | 0.98625
Langholm 33kV BB B |  |  |  | LAHO3B | LAHO3B | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99552 | 0.99552 | 0.98315 | 0.98315 | 0.98315 | 0.99743 | 0.99506 | 0.98614 | 0.98614 | 0.98614 | 0.98614 | 0.98614 | 0.98614 | 0.98614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99552 | 0.98315 | 0.99743 | 0.99506 | 0.98614
|  |  |  | WYSB0G | WYSB0G | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lockerbie 33/11kV T2 |  |  |  | LOBIT2 | LOBIT2 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91944 | 0.97356 | 0.95422 | 0.96204 | 0.96204 | 0.96204 | 0.96204 | 0.96204 | 0.96204 | 0.96204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91944 | 0.97356 | 0.95422 | 0.96204
Lockerbie 33kV BB B |  |  |  | LOBI3B | LOBI3B | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91945 | 0.97357 | 0.95422 | 0.96205 | 0.96205 | 0.96205 | 0.96205 | 0.96205 | 0.96205 | 0.96205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91945 | 0.97357 | 0.95422 | 0.96205
Kirbank 33/11kV T1 |  |  |  | KIBAT1 | KIBAT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89285 | 0.91499 | 0.9504 | 0.9504 | 0.9504 | 0.9504 | 0.9504 | 0.9504 | 0.9504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89285 | 0.91499 | 0.9504
Gretna 33kV BB B |  |  |  | GRNA3B | GRNA3B | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95358 | 0.97694 | 0.97694 | 0.96922 | 0.96922 | 0.96922 | 0.98366 | 0.98125 | 0.99191 | 0.99191 | 0.99191 | 0.99191 | 0.99191 | 0.99191 | 0.99191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95358 | 0.97694 | 0.96922 | 0.98366 | 0.98125 | 0.99191
Middlebie 33/11kV T1 |  |  |  | MIBIT1 | MIBIT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96473 | 0.96473 | 0.96473 | 0.96755 | 0.98635 | 0.98635 | 0.98357 | 0.98357 | 0.98357 | 0.99676 | 0.99503 | 1.0013 | 1.0013 | 1.0013 | 1.0013 | 1.0013 | 1.0013 | 1.0013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96473 | 0.96473 | 0.96755 | 0.98635 | 0.98357 | 0.99676 | 0.99503 | 1.0013
Moffat 33/11kV T1 |  |  |  | MOFTT1 | MOFTT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88126 | 0.90674 | 0.94403 | 0.94403 | 0.94403 | 0.94403 | 0.94403 | 0.94403 | 0.94403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88126 | 0.90674 | 0.94403
Chapelgross 33kV BB A2 |  |  | Y | CHAP3A2 | CHAP3A2 | 33 | 0 | 0 | 0 | 0 | 0 | 1.0152 | 1.0152 | 1.0161 | 1.0161 | 1.0204 | 1.0204 | 1.0204 | 1.0243 | 1.0243 | 1.0243 | 1.0243 | 1.0243 | 0.98422 | 0.98422 | 0.98033 | 0.98033 | 0.98033 | 0.99573 | 1.0053 | 1.0053 | 0.98674 | 0.98674 | 0.98674 | 1.0009 | 0.99855 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 0 | 0 | 1.0187 | 1.0152 | 1.0161 | 1.0204 | 1.0243 | 0.98422 | 0.98033 | 0.98033 | 0.99573 | 1.0053 | 0.98674 | 1.0009 | 0.99855 | 1.0037
Chapelgross 33kV BB A1 |  |  | Y | CHAP3A1 | CHAP3A1 | 33 | 0 | 0 | 0 | 0 | 0 | 1.0152 | 1.0152 | 1.0161 | 1.0161 | 1.0204 | 1.0204 | 1.0204 | 1.0243 | 1.0243 | 1.0243 | 1.0243 | 1.0243 | 0.98422 | 0.98422 | 0.98033 | 0.98033 | 0.98033 | 0.99573 | 1.0053 | 1.0053 | 0.98674 | 0.98674 | 0.98674 | 1.0009 | 0.99855 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 0 | 0 | 1.0187 | 1.0152 | 1.0161 | 1.0204 | 1.0243 | 0.98422 | 0.98033 | 0.98033 | 0.99573 | 1.0053 | 0.98674 | 1.0009 | 0.99855 | 1.0037
Gretna 33/11kV T2 |  |  |  | GRNAT2 | GRNAT2 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95358 | 0.97693 | 0.97693 | 0.96922 | 0.96922 | 0.96922 | 0.98366 | 0.98125 | 0.99191 | 0.99191 | 0.99191 | 0.99191 | 0.99191 | 0.99191 | 0.99191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95358 | 0.97693 | 0.96922 | 0.98366 | 0.98125 | 0.99191
Newcastleton 11kV BB |  |  |  | NEWC5- | NEWC5- | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0004 | 1.0004 | 0.99324 | 0.99324 | 0.99324 | 0.99265 | 0.99026 | 0.99629 | 0.99629 | 0.99629 | 0.99629 | 0.99629 | 0.99629 | 0.99629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0004 | 0.99324 | 0.99265 | 0.99026 | 0.99629
Annan 33/11kV T2 |  |  |  | ANANT2 | ANANT2 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97734 | 0.97548 | 0.97548 | 0.97548 | 0.99276 | 1.0024 | 1.0024 | 0.98374 | 0.98374 | 0.98374 | 0.99794 | 0.99558 | 1.0007 | 1.0007 | 1.0007 | 1.0007 | 1.0007 | 1.0007 | 1.0007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97734 | 0.97548 | 0.97548 | 0.99276 | 1.0024 | 0.98374 | 0.99794 | 0.99558 | 1.0007
Annan 11kV BB1 |  |  |  | ANAN5-1 | ANAN5-1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0042 | 1.0042 | 1.0055 | 1.0055 | 1.0055 | 1.0005 | 1.0102 | 1.0102 | 1.0035 | 1.0035 | 1.0035 | 1.0057 | 1.0033 | 1.0085 | 1.0085 | 1.0085 | 1.0085 | 1.0085 | 1.0085 | 1.0085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0042 | 1.0055 | 1.0055 | 1.0005 | 1.0102 | 1.0035 | 1.0057 | 1.0033 | 1.0085
Stevenscroft 33kV BB |  |  |  | STCR3- | STCR3- | 33 | 0 | 0 | 0 | 1.0156 | 1.0156 | 1.0132 | 1.0132 | 1.0141 | 1.0141 | 1.0171 | 1.0171 | 1.0171 | 1.0199 | 1.0199 | 1.0199 | 1.0199 | 1.0199 | 0.9983 | 0.9983 | 0.99658 | 0.99658 | 0.99658 | 1.0062 | 1.0116 | 1.0116 | 1.0031 | 1.0031 | 1.0031 | 1.0115 | 1.0104 | 1.013 | 1.013 | 1.013 | 1.013 | 1.013 | 1.013 | 1.013 | 1 | 1.0156 | 1.0156 | 1.0132 | 1.0141 | 1.0171 | 1.0199 | 0.9983 | 0.99658 | 0.99658 | 1.0062 | 1.0116 | 1.0031 | 1.0115 | 1.0104 | 1.013
Stevenscroft 11kV BB |  |  |  | STCR5- | STCR5- | 11 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Minsca 33kV WF BB |  |  | Y | MINS0G | MINS0G | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0089 | 1.0099 | 1.0099 | 1.0142 | 1.0142 | 1.0142 | 1.0181 | 1.0181 | 1.0181 | 1.0181 | 1.0181 | 0.97766 | 0.97766 | 0.97374 | 0.97374 | 0.97374 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 0 | 0 | 0 | 1.0089 | 1.0099 | 1.0142 | 1.0181 | 0.97766 | 0.97374 | 0.97374 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02
Ewe Hill |  |  |  | EWHC0G | EWHC0G | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0119 | 1.0162 | 1.0162 | 1.0162 | 1.0201 | 1.0201 | 1.0201 | 1.0201 | 1.0201 | 0.97964 | 0.97964 | 0.96009 | 0.96009 | 0.96009 | 0.96293 | 0.98185 | 0.98185 | 1.0101 | 1.0101 | 1.0101 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 0 | 0 | 0 | 0 | 1.0119 | 1.0162 | 1.0201 | 0.97964 | 0.96009 | 0.96009 | 0.96293 | 0.98185 | 1.0101 | 1.02 | 1.02 | 1.02
Lockerbie 11kV BB A |  |  |  | LOBI5-1 | LOBI5-1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0049 | 1.0049 | 1.0049 | 1.0018 | 1.0092 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0049 | 1.0018 | 1.0092 | 1.0061
Kirkbank 11kV |  |  |  | KIBA5- | KIBA5- | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9998 | 0.99098 | 0.99649 | 0.99649 | 0.99649 | 0.99649 | 0.99649 | 0.99649 | 0.99649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9998 | 0.99098 | 0.99649
Gretna 11kB BB B |  |  |  | GRNA5-2 | GRNA5-2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0009 | 1.0051 | 1.0051 | 1.0001 | 1.0001 | 1.0001 | 1.0027 | 1.0002 | 1.0093 | 1.0093 | 1.0093 | 1.0093 | 1.0093 | 1.0093 | 1.0093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0009 | 1.0051 | 1.0001 | 1.0027 | 1.0002 | 1.0093
Lockerbie 11kV BB B |  |  |  | LOBI5-2 | LOBI5-2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0011 | 1.0095 | 1.0149 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 1.0061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0011 | 1.0095 | 1.0149 | 1.0061
Annan 11kV BB2 |  |  |  | ANAN5-2 | ANAN5-2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0041 | 1.0054 | 1.0054 | 1.0054 | 1.0005 | 1.0102 | 1.0102 | 1.0035 | 1.0035 | 1.0035 | 1.0057 | 1.0033 | 1.0085 | 1.0085 | 1.0085 | 1.0085 | 1.0085 | 1.0085 | 1.0085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0041 | 1.0054 | 1.0054 | 1.0005 | 1.0102 | 1.0035 | 1.0057 | 1.0033 | 1.0085
Moffat 11kV BB B |  |  |  | MOFT5-2 | MOFT5-2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99283 | 0.99292 | 0.99292 | 0.99292 | 0.99292 | 0.99292 | 0.99292 | 0.99292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99283 | 0.99292
Middlebie 11kV BB |  |  |  | MIBI5- | MIBI5- | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0012 | 1.0012 | 1.0012 | 0.99314 | 0.99964 | 0.99964 | 0.99682 | 0.99682 | 0.99682 | 0.99755 | 0.99583 | 1.0021 | 1.0021 | 1.0021 | 1.0021 | 1.0021 | 1.0021 | 1.0021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0012 | 1.0012 | 0.99314 | 0.99964 | 0.99682 | 0.99755 | 0.99583 | 1.0021
N/A |  |  |  | CRAG0A | CRAG0A | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9858 | 1.007 | 1.007 | 1.0036 | 1.0036 | 1.0036 | 1.0058 | 1.0038 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9858 | 1.007 | 1.0036 | 1.0058 | 1.0038 | 1.0033
Langholm 11kV BB A |  |  |  | LAHO5-1 | LAHO5-1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9858 | 0.9858 | 1.007 | 1.007 | 1.0036 | 1.0036 | 1.0036 | 1.0058 | 1.0038 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9858 | 1.007 | 1.0036 | 1.0058 | 1.0038 | 1.0033
N/A |  |  |  | CRAG5A | CRAG5A | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9858 | 1.007 | 1.007 | 1.0036 | 1.0036 | 1.0036 | 1.0058 | 1.0038 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9858 | 1.007 | 1.0036 | 1.0058 | 1.0038 | 1.0033
N/A |  |  |  | CRAG5B | CRAG5B | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9858 | 1.007 | 1.007 | 1.0036 | 1.0036 | 1.0036 | 1.0058 | 1.0038 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9858 | 1.007 | 1.0036 | 1.0058 | 1.0038 | 1.0033
Ewehill 1 WF 33kV |  |  |  | EWEH3- | EWHC3- | 33 | 0 | 0 | 0 | 0 | 1.0153 | 1.0153 | 1.0153 | 1.0153 | 1.0153 | 1.0196 | 1.0196 | 1.0196 | 1.0235 | 1.0235 | 1.0235 | 1.0235 | 1.0235 | 0.98315 | 0.98315 | 0.96367 | 0.96367 | 0.96367 | 0.9665 | 0.98535 | 0.98535 | 0.99451 | 0.99451 | 0.99451 | 1.0069 | 1.0056 | 1.0105 | 1.0105 | 1.0105 | 1.0105 | 1.0105 | 1.0105 | 1.0105 | 0 | 0 | 0 | 0 | 1.0153 | 1.0196 | 1.0235 | 0.98315 | 0.96367 | 0.96367 | 0.9665 | 0.98535 | 0.99451 | 1.0069 | 1.0056 | 1.0105
Gretna 11kB BB A |  |  |  | GRNA5-1 | GRNA5-1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0009 | 1.0051 | 1.0051 | 1.0001 | 1.0001 | 1.0001 | 1.0027 | 1.0002 | 1.0093 | 1.0093 | 1.0093 | 1.0093 | 1.0093 | 1.0093 | 1.0093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0009 | 1.0051 | 1.0001 | 1.0027 | 1.0002 | 1.0093
Moffat 11kV BB A |  |  |  | MOFT5-1 | MOFT5-1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99168 | 0.99498 | 0.99292 | 0.99292 | 0.99292 | 0.99292 | 0.99292 | 0.99292 | 0.99292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99168 | 0.99498 | 0.99292
Langholm 11kV BB A |  |  |  | LAHO5-2 | LAHO5-2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9858 | 0.9858 | 1.007 | 1.007 | 1.0036 | 1.0036 | 1.0036 | 1.0058 | 1.0038 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9858 | 1.007 | 1.0036 | 1.0058 | 1.0038 | 1.0033
Minsca 33kV BB |  |  |  | MINS3- | MINS3- | 33 | 0 | 0 | 0 | 0 | 1.012 | 1.012 | 1.012 | 1.0129 | 1.0129 | 1.0172 | 1.0172 | 1.0172 | 1.0211 | 1.0211 | 1.0211 | 1.0211 | 1.0211 | 0.98081 | 0.98081 | 0.9769 | 0.9769 | 0.9769 | 1.0149 | 1.0187 | 1.0187 | 1.0113 | 1.0113 | 1.0113 | 1.0169 | 1.016 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 0 | 0 | 0 | 1.012 | 1.0129 | 1.0172 | 1.0211 | 0.98081 | 0.9769 | 0.9769 | 1.0149 | 1.0187 | 1.0113 | 1.0169 | 1.016 | 1.018
Lockerbie 33/11kV T1 |  |  |  | LOBIT1 | LOBIT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92033 | 0.92033 | 0.92033 | 0.94506 | 0.952 | 0.97311 | 0.97311 | 0.97311 | 0.97311 | 0.97311 | 0.97311 | 0.97311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92033 | 0.94506 | 0.952 | 0.97311
N/A |  |  |  | CRAG0G | CRAG0G | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9858 | 1.007 | 1.007 | 1.0036 | 1.0036 | 1.0036 | 1.0058 | 1.0038 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 1.0033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9858 | 1.007 | 1.0036 | 1.0058 | 1.0038 | 1.0033
Ewehill 1 WF 33kV BB |  |  | Y | EWEH0G | EWEH3- | 33 | 0 | 0 | 0 | 0 | 1.0191 | 1.0191 | 1.0191 | 1.0191 | 1.0191 | 0 | 0 | 0 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 0.8781 | 0.8781 | 0.87464 | 0.87464 | 0.87464 | 0.88838 | 1.0111 | 1.0111 | 0.88035 | 0.88035 | 0.88035 | 1.0066 | 0.89089 | 1.0094 | 1.0094 | 1.0094 | 1.0094 | 1.0094 | 1.0094 | 1.0094 | 1.0191 | 1.0191 | 1.0191 | 1.0191 | 1.0191 | 0 | 1.0129 | 0.8781 | 0.87464 | 0.87464 | 0.88838 | 1.0111 | 0.88035 | 1.0066 | 0.89089 | 1.0094
Ewehill 1 WF 33kV WF BB |  |  | Y | EWEH1Q | EWEH0G | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0191 | 1.0191 | 1.0191 | 1.0191 | 1.0191 | 0 | 1.0129 | 0.8781 | 0.87464 | 0.87464 | 0.88838 | 1.0111 | 0.88035 | 1.0066 | 0.89089 | 1.0094
Ewehill 2 WF 33kV WF BB |  |  | Y | EWEH0G_2 | EWEH1Q | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.013 | 0.79033 | 0.79033 | 0.78721 | 0.78721 | 0.78721 | 0.79957 | 0.99429 | 0.99429 | 0.79235 | 0.79235 | 0.79235 | 0.9899 | 0.80184 | 0.99265 | 0.99265 | 0.99265 | 0.99265 | 0.99265 | 0.99265 | 0.99265 | 1.0191 | 1.0191 | 1.0191 | 1.0191 | 1.0191 | 0 | 1.013 | 0.79033 | 0.78721 | 0.78721 | 0.79957 | 0.99429 | 0.79235 | 0.9899 | 0.80184 | 0.99265
N/A |  |  |  | BR001- | BR001- | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N/A |  |  |  | AL048A | AL048A | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0063 | 1.0063 | 1.0063 | 1.0128 | 1.0128 | 1.0128 | 1.0128 | 1.0128 | 0.79021 | 0.79021 | 0.78709 | 0.78709 | 0.78709 | 0.79945 | 0.99414 | 0.99414 | 0.79223 | 0.79223 | 0.79223 | 0.98975 | 0.80171 | 0.99249 | 0.99249 | 0.99249 | 0.99249 | 0.99249 | 0.99249 | 0.99249 | 0 | 0 | 0 | 0 | 0 | 1.0063 | 1.0128 | 0.79021 | 0.78709 | 0.78709 | 0.79945 | 0.99414 | 0.79223 | 0.98975 | 0.80171 | 0.99249
N/A |  |  |  | AL048B | AL048B | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014551 | 0.014646 | 0.011427 | 0.011382 | 0.011382 | 0.011561 | 0.014376 | 0.011457 | 0.014313 | 0.011594 | 0.014352
N/A |  |  |  | BV001A | BV001A | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N/A |  |  |  | BV001B | BV001B | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solway 33kV BB |  |  | Y | SOLWAY | SOLWAY | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gretna 400kV |  |  | Y | GRTNA4- | GRTNA4- | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
End Of Sheet
Busbars on SLD
Transformers
Busbars N/A
Busbars not shown
Not used
Vlookup

## Transformers - Loading
Transformers - Loading
Results
Transformers
[8 empty] | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[8 empty] | Loading (%) >>> | [36 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  |  | Name | MVA | HV (kV) | LV (kV) | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  |  | EWHC3-_EWHC0G_1 | 13 | 33 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6637 | 6.6637 | 6.6356 | 6.6356 | 6.6356 | 6.6099 | 6.6099 | 6.6099 | 6.6099 | 6.6099 | 6.8831 | 6.8831 | 7.0232 | 7.0232 | 7.1166 | 7.0025 | 6.8676 | 6.8676 | 42.1585 | 42.1585 | 42.1585 | 39.6089 | 40.8059 | 36.9253 | 36.9253 | 36.9253 | 36.9253 | 36.9253 | 36.9253 | 36.9253 | 0 | 0 | 0 | 0 | 6.6637 | 6.6356 | 6.6099 | 6.8831 | 7.0232 | 7.1166 | 7.0025 | 6.8676 | 42.1585 | 39.6089 | 40.8059 | 36.9253
|  |  |  | CRAG5A_CRAG0A_1 | 8.84 | 11 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.107e-07 | 1.2267e-07 | 1.253e-07 | 1.253e-07 | 1.2488e-07 | 1.2488e-07 | 1.2488e-07 | 1.2516e-07 | 1.2491e-07 | 1.2485e-07 | 1.2485e-07 | 1.2485e-07 | 1.2485e-07 | 1.2485e-07 | 1.2485e-07 | 1.2485e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.107e-07 | 1.2267e-07 | 1.253e-07 | 1.2488e-07 | 1.2516e-07 | 1.2491e-07 | 1.2485e-07
|  |  |  | LAHOT2_LAHO20_T2 | 12 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3581e-08 | 9.3581e-08 | 9.4803e-08 | 9.4803e-08 | 9.4803e-08 | 9.3761e-08 | 9.3538e-08 | 20.7882 | 20.7882 | 20.7882 | 20.7882 | 20.7882 | 20.7882 | 20.7882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3581e-08 | 9.4803e-08 | 9.3761e-08 | 9.3538e-08 | 20.7882
|  |  |  | CRAG5-_CRAG0B_1 | 2.66 | 11 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7972e-07 | 2.0002e-07 | 2.0447e-07 | 2.0447e-07 | 2.0376e-07 | 2.0376e-07 | 2.0376e-07 | 2.0424e-07 | 2.0381e-07 | 2.0371e-07 | 2.0371e-07 | 2.0371e-07 | 2.0371e-07 | 2.0371e-07 | 2.0371e-07 | 2.0371e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7972e-07 | 2.0002e-07 | 2.0447e-07 | 2.0376e-07 | 2.0424e-07 | 2.0381e-07 | 2.0371e-07
|  |  |  | GRNAT2_GRNA20_T2 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.3078 | 93.1148 | 93.1148 | 62.385 | 62.385 | 62.385 | 62.2263 | 62.3804 | 41.5984 | 41.5984 | 41.5984 | 41.5984 | 41.5984 | 41.5984 | 41.5984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.3078 | 93.1148 | 62.385 | 62.2263 | 62.3804 | 41.5984
|  |  |  | MOFTT2_MOFT20_T2 | 7.5 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.1163 | 34.2173 | 34.2173 | 34.2173 | 34.2173 | 34.2173 | 34.2173 | 34.2173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.1163 | 34.2173
|  |  |  | LOBIT2_LOBI20_T2 | 24 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.05 | 31.6508 | 32.2889 | 33.7172 | 33.7172 | 33.7172 | 33.7172 | 33.7172 | 33.7172 | 33.7172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.05 | 31.6508 | 32.2889 | 33.7172
|  |  |  | GRNAT1_GRNA10_T1 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062333 | 0.062333 | 0.061449 | 0.061449 | 0.061449 | 0.062338 | 0.062191 | 20.366 | 20.366 | 20.366 | 20.366 | 20.366 | 20.366 | 20.366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062333 | 0.061449 | 0.062338 | 0.062191 | 20.366
|  |  |  | MIBIT1_MIBI10_T1 | 10 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.7528 | 108.7528 | 82.5344 | 54.114 | 53.0818 | 53.0818 | 53.232 | 53.232 | 53.232 | 52.5279 | 52.619 | 52.2901 | 52.2901 | 52.2901 | 52.2901 | 52.2901 | 52.2901 | 52.2901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.7528 | 82.5344 | 54.114 | 53.0818 | 53.232 | 52.5279 | 52.619 | 52.2901
|  |  |  | LAHOT1_LAHO10_T1 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138.0996 | 93.4875 | 57.8194 | 57.8194 | 58.0132 | 58.0132 | 58.0132 | 57.1318 | 57.2486 | 35.4709 | 35.4709 | 35.4709 | 35.4709 | 35.4709 | 35.4709 | 35.4709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138.0996 | 93.4875 | 57.8194 | 58.0132 | 57.1318 | 57.2486 | 35.4709
|  |  |  | NEWCT1_NEWC10_T1 | 5 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.2991 | 44.2991 | 22.3099 | 22.3099 | 22.3099 | 21.9884 | 22.0413 | 22.2417 | 22.2417 | 22.2417 | 22.2417 | 22.2417 | 22.2417 | 22.2417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.2991 | 22.3099 | 21.9884 | 22.0413 | 22.2417
|  |  |  | KIBAT1_KIBA10_T1 | 5 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.3616 | 44.9249 | 28.8488 | 28.8488 | 28.8488 | 28.8488 | 28.8488 | 28.8488 | 28.8488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.3616 | 44.9249 | 28.8488
|  |  |  | CHAP1-_CHAP3-_1 | 90 | 132 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1195 | 1.1195 | 1.1195 | 2.1494 | 2.1494 | 2.1494 | 2.1494 | 2.1494 | 1.6869 | 1.6869 | 1.6803 | 1.6803 | 1.7101 | 1.7067 | 2.1269 | 2.1269 | 1.6913 | 1.6913 | 1.6913 | 2.1175 | 1.7115 | 2.1234 | 2.1234 | 2.1234 | 2.1234 | 2.1234 | 2.1234 | 2.1234 | 0 | 0 | 0 | 0 | 0 | 1.1195 | 2.1494 | 1.6869 | 1.6803 | 1.7101 | 1.7067 | 2.1269 | 1.6913 | 2.1175 | 1.7115 | 2.1234
|  |  |  | CHAP1-_CHAP3-_2 | 90 | 132 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | WYSB3-_WYSB0G_1 | 12.5 | 33 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | STCR3-_STCR5-_1 | 50 | 33 | 11 | 0 | 0 | 1e-10 | 10.3705 | 10.3705 | 8.9653 | 8.9653 | 9.7783 | 9.7783 | 11.7885 | 11.7885 | 11.7885 | 13.692 | 13.692 | 13.692 | 13.692 | 13.692 | 52.3528 | 52.3528 | 61.7773 | 61.7773 | 35.6476 | 50.9451 | 40.0843 | 40.0843 | 83.7838 | 83.7838 | 83.7838 | 67.2917 | 72.8425 | 62.9666 | 62.9666 | 62.9666 | 62.9666 | 62.9666 | 62.9666 | 62.9666 | 2.2e-08 | 10.3705 | 10.3705 | 8.9653 | 9.7783 | 11.7885 | 13.692 | 52.3528 | 61.7773 | 35.6476 | 50.9451 | 40.0843 | 83.7838 | 67.2917 | 72.8425 | 62.9666
|  |  |  | ANANT1_ANAN10_T1 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.1168 | 105.1168 | 78.7371 | 78.7371 | 52.6469 | 52.7551 | 52.245 | 52.245 | 52.5963 | 52.5963 | 52.5963 | 52.4794 | 52.6044 | 52.5875 | 52.5875 | 52.5875 | 52.5875 | 52.5875 | 52.5875 | 52.5875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.1168 | 78.7371 | 52.6469 | 52.7551 | 52.245 | 52.5963 | 52.4794 | 52.6044 | 52.5875
|  |  |  | ANANT2_ANAN20_T2 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.1319 | 78.7418 | 78.7418 | 52.6473 | 52.7555 | 52.2453 | 52.2453 | 52.5967 | 52.5967 | 52.5967 | 52.4798 | 52.6049 | 52.078 | 52.078 | 52.078 | 52.078 | 52.078 | 52.078 | 52.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.1319 | 78.7418 | 52.6473 | 52.7555 | 52.2453 | 52.5967 | 52.4798 | 52.6049 | 52.078
|  |  |  | MINS3-_MINS0G_1 | 44.2 | 33 | 0.69 | 0 | 0 | 0 | 0 | 0 | 6.1575 | 6.1575 | 6.1516 | 6.1516 | 6.1256 | 6.1256 | 6.1256 | 6.1019 | 6.1019 | 6.1019 | 6.1019 | 6.1019 | 6.3544 | 6.3544 | 6.38 | 6.38 | 43.8064 | 44.0881 | 43.2629 | 43.2629 | 45.9979 | 45.9979 | 45.9979 | 43.4815 | 43.711 | 43.3116 | 43.3116 | 43.3116 | 43.3116 | 43.3116 | 43.3116 | 43.3116 | 0 | 0 | 0 | 6.1575 | 6.1516 | 6.1256 | 6.1019 | 6.3544 | 6.38 | 43.8064 | 44.0881 | 43.2629 | 45.9979 | 43.4815 | 43.711 | 43.3116
|  |  |  | LOBIT1_LOBI10_T1 | 24 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.514 | 67.514 | 67.514 | 32.5072 | 32.2661 | 31.2143 | 31.2143 | 31.2143 | 31.2143 | 31.2143 | 31.2143 | 31.2143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.514 | 32.5072 | 32.2661 | 31.2143
|  |  |  | MOFTT1_MOFT10_T1 | 7.5 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.0582 | 47.3522 | 27.4521 | 27.4521 | 27.4521 | 27.4521 | 27.4521 | 27.4521 | 27.4521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.0582 | 47.3522 | 27.4521
|  |  |  | trf_EWEH1Q_EWEH3-_1 | 90 | 132 | 33 | 0 | 0 | 0.03801 | 0.03801 | 0.03801 | 0.03801 | 0.03801 | 0.03801 | 0.03801 | 0 | 0 | 0 | 0.037781 | 0.037781 | 0.037781 | 0.037781 | 0.037781 | 0.036392 | 0.036392 | 0.036248 | 0.036248 | 0.036892 | 0.036817 | 0.038352 | 0.038352 | 0.036485 | 0.036485 | 0.036485 | 0.038183 | 0.036921 | 0.038289 | 0.038289 | 0.038289 | 0.038289 | 0.038289 | 0.038289 | 0.038289 | 0.03801 | 0.03801 | 0.03801 | 0.03801 | 0.03801 | 0 | 0.037781 | 0.036392 | 0.036248 | 0.036892 | 0.036817 | 0.038352 | 0.036485 | 0.038183 | 0.036921 | 0.038289
|  |  | Y | trf_EWEH3-_EWEH0G_1 | 43.1667 | 33 | 0.69 | 0 | 0 | 2.5969e-08 | 2.5969e-08 | 2.5969e-08 | 2.5969e-08 | 2.5969e-08 | 2.5969e-08 | 2.5969e-08 | 0 | 0 | 0 | 2.5812e-08 | 2.5812e-08 | 2.5812e-08 | 2.5812e-08 | 2.5812e-08 | 2.2376e-08 | 2.2376e-08 | 2.2288e-08 | 2.2288e-08 | 2.2684e-08 | 2.2638e-08 | 2.5765e-08 | 2.5765e-08 | 2.2434e-08 | 2.2434e-08 | 2.2434e-08 | 2.5652e-08 | 2.2702e-08 | 2.5723e-08 | 2.5723e-08 | 2.5723e-08 | 2.5723e-08 | 2.5723e-08 | 2.5723e-08 | 2.5723e-08 | 2.5969e-08 | 2.5969e-08 | 2.5969e-08 | 2.5969e-08 | 2.5969e-08 | 0 | 2.5812e-08 | 2.2376e-08 | 2.2288e-08 | 2.2684e-08 | 2.2638e-08 | 2.5765e-08 | 2.2434e-08 | 2.5652e-08 | 2.2702e-08 | 2.5723e-08
|  |  |  | tr3_GRNA4-_GRNA1-_1 | 240 | 400 | 33 | 0 | 0 | 17.0218 | 17.0218 | 17.0218 | 17.0218 | 17.0218 | 17.0218 | 17.0218 | 0 | 0 | 0 | 0.035375 | 0.035375 | 0.035375 | 0.035375 | 0.035375 | 0.019935 | 0.019935 | 0.019856 | 0.019856 | 0.020209 | 0.020168 | 0.024913 | 0.024913 | 0.019986 | 0.019986 | 0.019986 | 0.024815 | 0.020225 | 0.024883 | 0.024883 | 0.024883 | 0.024883 | 0.024883 | 0.024883 | 0.024883 | 17.0218 | 17.0218 | 17.0218 | 17.0218 | 17.0218 | 0 | 0.035375 | 0.019935 | 0.019856 | 0.020209 | 0.020168 | 0.024913 | 0.019986 | 0.024815 | 0.020225 | 0.024883
|  |  |  | tr3_GRNA4-_GRNA1-_2 | 240 | 400 | 33 | 0 | 0 | 17.5028 | 17.5028 | 17.5028 | 17.5028 | 17.5028 | 17.5028 | 17.5028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.5028 | 17.5028 | 17.5028 | 17.5028 | 17.5028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | STCR0G-_STCRLV | 999 | 11 | 0.4 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | CHAP3-AUX-_1 | 999 | 33 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
Vlookup
End Of Sheet
Note on AA26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: cells in yellow: manual value

## Transformers - MVA
Transformers - MVA
Results
Transformers
[7 empty] | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[7 empty] | Loading (MVA) >>> | [36 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  | Name | MVA | HV (kV) | LV (kV) | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  | EWHC3-_EWHC0G_1 | 13 | 33 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86629 | 0.86629 | 0.86263 | 0.86263 | 0.86263 | 0.85929 | 0.85929 | 0.85929 | 0.85929 | 0.85929 | 0.8948 | 0.8948 | 0.91302 | 0.91302 | 0.92515 | 0.91033 | 0.89279 | 0.89279 | 5.4806 | 5.4806 | 5.4806 | 5.1492 | 5.3048 | 4.8003 | 4.8003 | 4.8003 | 4.8003 | 4.8003 | 4.8003 | 4.8003 | 0 | 0 | 0 | 0 | 0.86629 | 0.86263 | 0.85929 | 0.8948 | 0.91302 | 0.92515 | 0.91033 | 0.89279 | 5.4806 | 5.1492 | 5.3048 | 4.8003
|  |  | CRAG5A_CRAG0A_1 | 8.84 | 11 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.786e-09 | 1.0844e-08 | 1.1077e-08 | 1.1077e-08 | 1.104e-08 | 1.104e-08 | 1.104e-08 | 1.1064e-08 | 1.1042e-08 | 1.1037e-08 | 1.1037e-08 | 1.1037e-08 | 1.1037e-08 | 1.1037e-08 | 1.1037e-08 | 1.1037e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.786e-09 | 1.0844e-08 | 1.1077e-08 | 1.104e-08 | 1.1064e-08 | 1.1042e-08 | 1.1037e-08
|  |  | LAHOT2_LAHO20_T2 | 12 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.123e-08 | 1.123e-08 | 1.1376e-08 | 1.1376e-08 | 1.1376e-08 | 1.1251e-08 | 1.1225e-08 | 2.4946 | 2.4946 | 2.4946 | 2.4946 | 2.4946 | 2.4946 | 2.4946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.123e-08 | 1.1376e-08 | 1.1251e-08 | 1.1225e-08 | 2.4946
|  |  | CRAG5-_CRAG0B_1 | 2.66 | 11 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7806e-09 | 5.3205e-09 | 5.439e-09 | 5.439e-09 | 5.4201e-09 | 5.4201e-09 | 5.4201e-09 | 5.4327e-09 | 5.4212e-09 | 5.4186e-09 | 5.4186e-09 | 5.4186e-09 | 5.4186e-09 | 5.4186e-09 | 5.4186e-09 | 5.4186e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7806e-09 | 5.3205e-09 | 5.439e-09 | 5.4201e-09 | 5.4327e-09 | 5.4212e-09 | 5.4186e-09
|  |  | GRNAT2_GRNA20_T2 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.1569 | 11.1738 | 11.1738 | 7.4862 | 7.4862 | 7.4862 | 7.4672 | 7.4856 | 4.9918 | 4.9918 | 4.9918 | 4.9918 | 4.9918 | 4.9918 | 4.9918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.1569 | 11.1738 | 7.4862 | 7.4672 | 7.4856 | 4.9918
|  |  | MOFTT2_MOFT20_T2 | 7.5 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8087 | 2.5663 | 2.5663 | 2.5663 | 2.5663 | 2.5663 | 2.5663 | 2.5663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8087 | 2.5663
|  |  | LOBIT2_LOBI20_T2 | 24 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.332 | 7.5962 | 7.7493 | 8.0921 | 8.0921 | 8.0921 | 8.0921 | 8.0921 | 8.0921 | 8.0921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.332 | 7.5962 | 7.7493 | 8.0921
|  |  | GRNAT1_GRNA10_T1 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00748 | 0.00748 | 0.0073739 | 0.0073739 | 0.0073739 | 0.0074806 | 0.0074629 | 2.4439 | 2.4439 | 2.4439 | 2.4439 | 2.4439 | 2.4439 | 2.4439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00748 | 0.0073739 | 0.0074806 | 0.0074629 | 2.4439
|  |  | MIBIT1_MIBI10_T1 | 10 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8753 | 10.8753 | 8.2534 | 5.4114 | 5.3082 | 5.3082 | 5.3232 | 5.3232 | 5.3232 | 5.2528 | 5.2619 | 5.229 | 5.229 | 5.229 | 5.229 | 5.229 | 5.229 | 5.229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8753 | 8.2534 | 5.4114 | 5.3082 | 5.3232 | 5.2528 | 5.2619 | 5.229
|  |  | LAHOT1_LAHO10_T1 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.572 | 11.2185 | 6.9383 | 6.9383 | 6.9616 | 6.9616 | 6.9616 | 6.8558 | 6.8698 | 4.2565 | 4.2565 | 4.2565 | 4.2565 | 4.2565 | 4.2565 | 4.2565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.572 | 11.2185 | 6.9383 | 6.9616 | 6.8558 | 6.8698 | 4.2565
|  |  | NEWCT1_NEWC10_T1 | 5 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.215 | 2.215 | 1.1155 | 1.1155 | 1.1155 | 1.0994 | 1.1021 | 1.1121 | 1.1121 | 1.1121 | 1.1121 | 1.1121 | 1.1121 | 1.1121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.215 | 1.1155 | 1.0994 | 1.1021 | 1.1121
|  |  | KIBAT1_KIBA10_T1 | 5 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0681 | 2.2462 | 1.4424 | 1.4424 | 1.4424 | 1.4424 | 1.4424 | 1.4424 | 1.4424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0681 | 2.2462 | 1.4424
|  |  | CHAP1-_CHAP3-_1 | 90 | 132 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0076 | 1.0076 | 1.0076 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 1.9344 | 1.5183 | 1.5183 | 1.5123 | 1.5123 | 1.5391 | 1.536 | 1.9143 | 1.9143 | 1.5221 | 1.5221 | 1.5221 | 1.9058 | 1.5404 | 1.9111 | 1.9111 | 1.9111 | 1.9111 | 1.9111 | 1.9111 | 1.9111 | 0 | 0 | 0 | 0 | 0 | 1.0076 | 1.9344 | 1.5183 | 1.5123 | 1.5391 | 1.536 | 1.9143 | 1.5221 | 1.9058 | 1.5404 | 1.9111
|  |  | CHAP1-_CHAP3-_2 | 90 | 132 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | WYSB3-_WYSB0G_1 | 12.5 | 33 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875
|  |  | STCR3-_STCR5-_1 | 50 | 33 | 11 | 0 | 0 | 5e-11 | 5.1853 | 5.1853 | 4.4826 | 4.4826 | 4.8892 | 4.8892 | 5.8942 | 5.8942 | 5.8942 | 6.846 | 6.846 | 6.846 | 6.846 | 6.846 | 26.1764 | 26.1764 | 30.8886 | 30.8886 | 17.8238 | 25.4725 | 20.0421 | 20.0421 | 41.8919 | 41.8919 | 41.8919 | 33.6459 | 36.4212 | 31.4833 | 31.4833 | 31.4833 | 31.4833 | 31.4833 | 31.4833 | 31.4833 | 1.1e-08 | 5.1853 | 5.1853 | 4.4826 | 4.8892 | 5.8942 | 6.846 | 26.1764 | 30.8886 | 17.8238 | 25.4725 | 20.0421 | 41.8919 | 33.6459 | 36.4212 | 31.4833
|  |  | ANANT1_ANAN10_T1 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.614 | 12.614 | 9.4485 | 9.4485 | 6.3176 | 6.3306 | 6.2694 | 6.2694 | 6.3116 | 6.3116 | 6.3116 | 6.2975 | 6.3125 | 6.3105 | 6.3105 | 6.3105 | 6.3105 | 6.3105 | 6.3105 | 6.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.614 | 9.4485 | 6.3176 | 6.3306 | 6.2694 | 6.3116 | 6.2975 | 6.3125 | 6.3105
|  |  | ANANT2_ANAN20_T2 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6158 | 9.449 | 9.449 | 6.3177 | 6.3307 | 6.2694 | 6.2694 | 6.3116 | 6.3116 | 6.3116 | 6.2976 | 6.3126 | 6.2494 | 6.2494 | 6.2494 | 6.2494 | 6.2494 | 6.2494 | 6.2494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6158 | 9.449 | 6.3177 | 6.3307 | 6.2694 | 6.3116 | 6.2976 | 6.3126 | 6.2494
|  |  | MINS3-_MINS0G_1 | 44.2 | 33 | 0.69 | 0 | 0 | 0 | 0 | 0 | 2.7216 | 2.7216 | 2.719 | 2.719 | 2.7075 | 2.7075 | 2.7075 | 2.697 | 2.697 | 2.697 | 2.697 | 2.697 | 2.8086 | 2.8086 | 2.82 | 2.82 | 19.3624 | 19.4869 | 19.1222 | 19.1222 | 20.3311 | 20.3311 | 20.3311 | 19.2188 | 19.3203 | 19.1437 | 19.1437 | 19.1437 | 19.1437 | 19.1437 | 19.1437 | 19.1437 | 0 | 0 | 0 | 2.7216 | 2.719 | 2.7075 | 2.697 | 2.8086 | 2.82 | 19.3624 | 19.4869 | 19.1222 | 20.3311 | 19.2188 | 19.3203 | 19.1437
|  |  | LOBIT1_LOBI10_T1 | 24 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.2034 | 16.2034 | 16.2034 | 7.8017 | 7.7439 | 7.4914 | 7.4914 | 7.4914 | 7.4914 | 7.4914 | 7.4914 | 7.4914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.2034 | 7.8017 | 7.7439 | 7.4914
|  |  | MOFTT1_MOFT10_T1 | 7.5 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8794 | 3.5514 | 2.0589 | 2.0589 | 2.0589 | 2.0589 | 2.0589 | 2.0589 | 2.0589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8794 | 3.5514 | 2.0589
|  |  | trf_EWEH1Q_EWEH3-_1 | 90 | 132 | 33 | 0 | 0 | 0.034209 | 0.034209 | 0.034209 | 0.034209 | 0.034209 | 0.034209 | 0.034209 | 0 | 0 | 0 | 0.034003 | 0.034003 | 0.034003 | 0.034003 | 0.034003 | 0.032753 | 0.032753 | 0.032623 | 0.032623 | 0.033203 | 0.033135 | 0.034517 | 0.034517 | 0.032836 | 0.032836 | 0.032836 | 0.034364 | 0.033229 | 0.03446 | 0.03446 | 0.03446 | 0.03446 | 0.03446 | 0.03446 | 0.03446 | 0.034209 | 0.034209 | 0.034209 | 0.034209 | 0.034209 | 0 | 0.034003 | 0.032753 | 0.032623 | 0.033203 | 0.033135 | 0.034517 | 0.032836 | 0.034364 | 0.033229 | 0.03446
|  |  | trf_EWEH3-_EWEH0G_1 | 43.1667 | 33 | 0.69 | 0 | 0 | 1.121e-08 | 1.121e-08 | 1.121e-08 | 1.121e-08 | 1.121e-08 | 1.121e-08 | 1.121e-08 | 0 | 0 | 0 | 1.1142e-08 | 1.1142e-08 | 1.1142e-08 | 1.1142e-08 | 1.1142e-08 | 9.6592e-09 | 9.6592e-09 | 9.621e-09 | 9.621e-09 | 9.792e-09 | 9.7721e-09 | 1.1122e-08 | 1.1122e-08 | 9.6839e-09 | 9.6839e-09 | 9.6839e-09 | 1.1073e-08 | 9.7998e-09 | 1.1104e-08 | 1.1104e-08 | 1.1104e-08 | 1.1104e-08 | 1.1104e-08 | 1.1104e-08 | 1.1104e-08 | 1.121e-08 | 1.121e-08 | 1.121e-08 | 1.121e-08 | 1.121e-08 | 0 | 1.1142e-08 | 9.6592e-09 | 9.621e-09 | 9.792e-09 | 9.7721e-09 | 1.1122e-08 | 9.6839e-09 | 1.1073e-08 | 9.7998e-09 | 1.1104e-08
|  |  | tr3_GRNA4-_GRNA1-_1 | 240 | 400 | 33 | 0 | 0 | 40.8524 | 40.8524 | 40.8524 | 40.8524 | 40.8524 | 40.8524 | 40.8524 | 0 | 0 | 0 | 0.0849 | 0.0849 | 0.0849 | 0.0849 | 0.0849 | 0.047843 | 0.047843 | 0.047654 | 0.047654 | 0.048501 | 0.048403 | 0.059792 | 0.059792 | 0.047966 | 0.047966 | 0.047966 | 0.059555 | 0.04854 | 0.059719 | 0.059719 | 0.059719 | 0.059719 | 0.059719 | 0.059719 | 0.059719 | 40.8524 | 40.8524 | 40.8524 | 40.8524 | 40.8524 | 0 | 0.0849 | 0.047843 | 0.047654 | 0.048501 | 0.048403 | 0.059792 | 0.047966 | 0.059555 | 0.04854 | 0.059719
|  |  | tr3_GRNA4-_GRNA1-_2 | 240 | 400 | 33 | 0 | 0 | 42.0067 | 42.0067 | 42.0067 | 42.0067 | 42.0067 | 42.0067 | 42.0067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.0067 | 42.0067 | 42.0067 | 42.0067 | 42.0067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | STCR0G-_STCRLV | 999 | 11 | 0.4 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | CHAP3-AUX-_1 | 999 | 33 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
Vlookup
End Of Sheet

## Transformers - Taps
Transformers - Taps
Results
Transformers
[8 empty] | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[8 empty] | Current Tap >>> | [36 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  | Name | HV (kV) | LV (kV) | Min Tap | Max Tap | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  | EWHC3-_EWHC0G_1 | 33 | 0.69 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | CRAG5A_CRAG0A_1 | 11 | 0.69 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | LAHOT2_LAHO20_T2 | 33 | 11 | 1 | 17 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 7 | 7 | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 7 | 8 | 8 | 8
|  |  | CRAG5-_CRAG0B_1 | 11 | 0.69 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | GRNAT2_GRNA20_T2 | 33 | 11.5 | 1 | 17 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 10 | 10 | 11 | 11 | 11
|  |  | MOFTT2_MOFT20_T2 | 33 | 11.5 | 1 | 17 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 4 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 4 | 8
|  |  | LOBIT2_LOBI20_T2 | 33 | 11.5 | 1 | 17 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 4 | 4 | 4 | 9 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 4 | 9 | 7 | 7
|  |  | GRNAT1_GRNA10_T1 | 33 | 11.5 | 1 | 17 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
|  |  | MIBIT1_MIBI10_T1 | 33 | 11 | 1 | 17 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 6 | 6 | 7 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 6 | 7 | 8 | 8 | 9 | 9 | 9
|  |  | LAHOT1_LAHO10_T1 | 33 | 11.5 | 1 | 17 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 1 | 1 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 1 | 1 | 5 | 5 | 6 | 6 | 8
|  |  | NEWCT1_NEWC10_T1 | 33 | 11 | -11 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | 0 | 0 | -1
|  |  | KIBAT1_KIBA10_T1 | 33 | 11 | -7 | 7 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -7 | -5 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -7 | -5 | -3
|  |  | CHAP1-_CHAP3-_1 | 132 | 33 | 1 | 19 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 19 | 19 | 19 | 19 | 19 | 19 | 8 | 8 | 19 | 19 | 19 | 8 | 19 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 19 | 19 | 19 | 19 | 8 | 19 | 8 | 19 | 8
|  |  | CHAP1-_CHAP3-_2 | 132 | 33 | 1 | 19 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  | WYSB3-_WYSB0G_1 | 33 | 0.69 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | STCR3-_STCR5-_1 | 33 | 11 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ANANT1_ANAN10_T1 | 33 | 11.5 | 1 | 17 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 10 | 10 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 12 | 12 | 12 | 11 | 12 | 12 | 12
|  |  | ANANT2_ANAN20_T2 | 33 | 11.5 | 1 | 17 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 10 | 10 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 12 | 12 | 12 | 11 | 12 | 12 | 12
|  |  | MINS3-_MINS0G_1 | 33 | 0.69 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | LOBIT1_LOBI10_T1 | 33 | 11 | 1 | 17 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 1 | 1 | 1 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 1 | 4 | 4 | 7
|  |  | MOFTT1_MOFT10_T1 | 33 | 11.5 | 1 | 17 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 3 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 3 | 5 | 8
|  |  | trf_EWEH1Q_EWEH3-_1 | 132 | 33 | 1 | 19 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 14 | 14 | 14 | 13 | 13 | 13 | 13 | 13 | 19 | 19 | 19 | 19 | 19 | 19 | 14 | 14 | 19 | 19 | 19 | 14 | 19 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 13 | 13 | 13 | 13 | 13 | 14 | 13 | 19 | 19 | 19 | 19 | 14 | 19 | 14 | 19 | 14
|  |  | trf_EWEH3-_EWEH0G_1 | 33 | 0.69 | -2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | tr3_GRNA4-_GRNA1-_1 | 400 | 33 | 1 | 15 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | tr3_GRNA4-_GRNA1-_2 | 400 | 33 | 1 | 15 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  |  | STCR0G-_STCRLV | 999 | 11 | 0.4 |  | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | CHAP3-AUX-_1 | 999 | 33 | 0.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
Vlookup
End Of Sheet

## Lines - Loading
Lines - Loading
Results
Lines
|  |  | Name in Simulation SLD | PowerFactory name | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[5 empty] | Loading (%) >>> | Value should be > 0 | [35 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  | network | Name |  | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  |  | lne_CHAP1-_HAKB1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | CRAG5B_LAHO5-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7206e-07 | 4.1317e-07 | 4.222e-07 | 4.222e-07 | 4.2076e-07 | 4.2076e-07 | 4.2076e-07 | 4.2173e-07 | 4.2085e-07 | 4.2065e-07 | 4.2065e-07 | 4.2065e-07 | 4.2065e-07 | 4.2065e-07 | 4.2065e-07 | 4.2065e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7206e-07 | 4.1317e-07 | 4.222e-07 | 4.2076e-07 | 4.2173e-07 | 4.2085e-07 | 4.2065e-07
|  |  | CHAPX3_LAHO3B_1 | CHAPX3_LAHO3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0371 | 9.0371 | 4.55 | 4.55 | 4.55 | 4.4844 | 4.4952 | 14.6709 | 14.6709 | 14.6709 | 14.6709 | 14.6709 | 14.6709 | 14.6709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0371 | 4.55 | 4.4844 | 4.4952 | 14.6709
|  |  | LOBI3B_MOFTT2_1 | LOBI3B_MOFTT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.3609 | 23.5393 | 23.5393 | 23.5393 | 23.5393 | 23.5393 | 23.5393 | 23.5393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.3609 | 23.5393
|  |  |  | lne_CHAP1-_DUMF1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | CHAP3-_LOBI3B_1 | CHAP3-_LOBI3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2934 | 36.4151 | 60.1453 | 50.1716 | 50.1716 | 50.1716 | 50.1716 | 50.1716 | 50.1716 | 50.1716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2934 | 36.4151 | 60.1453 | 50.1716
|  |  |  | CHAP3-_CHAPX1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.7042 | 65.7042 | 65.7042 | 63.8171 | 54.8749 | 44.4616 | 44.4616 | 44.4616 | 44.4616 | 44.4616 | 44.4616 | 44.4616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.7042 | 63.8171 | 54.8749 | 44.4616
|  |  | CHAPX4_KIBAT1_1 | CHAPX4_KIBAT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.344 | 12.7438 | 8.2592 | 8.2592 | 8.2592 | 8.2592 | 8.2592 | 8.2592 | 8.2592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.344 | 12.7438 | 8.2592
|  |  | CHAPX4_MOFTT1_1 | CHAPX4_MOFTT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.443 | 19.9742 | 11.5799 | 11.5799 | 11.5799 | 11.5799 | 11.5799 | 11.5799 | 11.5799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.443 | 19.9742 | 11.5799
|  |  | CHAP3-_CHAPX3_1 | CHAP3-_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0544 | 9.0544 | 4.8419 | 4.8419 | 4.8419 | 4.7936 | 4.8014 | 24.5514 | 24.5514 | 24.5514 | 24.5514 | 24.5514 | 24.5514 | 24.5514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0544 | 4.8419 | 4.7936 | 4.8014 | 24.5514
|  |  | GRNA3A_GRNAT1_1 | GRNA3A_GRNAT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.23938 | 0.23938 | 0.23938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074875 | 0.00073813 | 0.00074881 | 0.00074704 | 0.23938
|  |  | LOBI3A_LOBIT1_1 | LOBI3A_LOBIT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.622 | 1.622 | 1.622 | 0.78095 | 0.77516 | 0.74989 | 0.74989 | 0.74989 | 0.74989 | 0.74989 | 0.74989 | 0.74989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.622 | 0.78095 | 0.77516 | 0.74989
|  |  |  | LAHO3A_LAHOT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6589 | 1.123 | 0.69453 | 0.69453 | 0.69686 | 0.69686 | 0.69686 | 0.68627 | 0.68767 | 0.42608 | 0.42608 | 0.42608 | 0.42608 | 0.42608 | 0.42608 | 0.42608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6589 | 1.123 | 0.69453 | 0.69686 | 0.68627 | 0.68767 | 0.42608
|  |  |  | LAHO3B_LAHOT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2203e-09 | 2.2203e-09 | 2.2213e-09 | 2.2213e-09 | 2.2213e-09 | 2.2245e-09 | 2.2192e-09 | 0.24971 | 0.24971 | 0.24971 | 0.24971 | 0.24971 | 0.24971 | 0.24971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2203e-09 | 2.2213e-09 | 2.2245e-09 | 2.2192e-09 | 0.24971
|  |  | MIBI3-_MIBIT1_1 | MIBI3-_MIBIT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0886 | 1.0886 | 0.82617 | 0.54168 | 0.53135 | 0.53135 | 0.53285 | 0.53285 | 0.53285 | 0.5258 | 0.52672 | 0.52342 | 0.52342 | 0.52342 | 0.52342 | 0.52342 | 0.52342 | 0.52342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0886 | 0.82617 | 0.54168 | 0.53135 | 0.53285 | 0.5258 | 0.52672 | 0.52342
|  |  | GRNA3B_GRNAT2_1 | GRNA3B_GRNAT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5172 | 1.1053 | 1.1053 | 0.74078 | 0.74078 | 0.74078 | 0.72989 | 0.7317 | 0.48818 | 0.48818 | 0.48818 | 0.48818 | 0.48818 | 0.48818 | 0.48818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5172 | 1.1053 | 0.74078 | 0.72989 | 0.7317 | 0.48818
|  |  | MIBI3-_LAHO3A_1 | MIBI3-_LAHO3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149.4315 | 101.1587 | 62.5638 | 62.5638 | 62.7735 | 62.7735 | 62.7735 | 61.8198 | 61.9462 | 38.3815 | 38.3815 | 38.3815 | 38.3815 | 38.3815 | 38.3815 | 38.3815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149.4315 | 101.1587 | 62.5638 | 62.7735 | 61.8198 | 61.9462 | 38.3815
|  |  | LAHO3B_NEWCT1_1 | LAHO3B_NEWCT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0543 | 9.0543 | 4.5599 | 4.5599 | 4.5599 | 4.4942 | 4.505 | 4.546 | 4.546 | 4.546 | 4.546 | 4.546 | 4.546 | 4.546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0543 | 4.5599 | 4.4942 | 4.505 | 4.546
|  |  | CHAP3-_MIBI3-_1 | CHAP3-_MIBI3-_1 | 0 | 0 | 0 | 0 | 2.8426 | 2.8426 | 2.8426 | 2.8426 | 2.8535 | 2.8426 | 2.8426 | 2.8426 | 2.8535 | 2.8535 | 2.8535 | 2.8535 | 2.8535 | 2.7595 | 2.7595 | 54.6199 | 54.6199 | 119.9609 | 81.4607 | 60.7838 | 60.7838 | 39.909 | 39.909 | 39.909 | 38.499 | 39.0634 | 24.9359 | 24.9359 | 24.9359 | 24.9359 | 24.9359 | 24.9359 | 24.9359 | 0 | 0 | 0 | 0 | 2.8311 | 2.8426 | 2.8535 | 2.7595 | 54.6199 | 119.9609 | 81.4607 | 60.7838 | 39.909 | 38.499 | 39.0634 | 24.9359
|  |  | ANANT1_CHAP3-_1 | ANANT1_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.7552 | 59.7552 | 44.7683 | 44.7683 | 29.2243 | 29.2842 | 29.0018 | 29.0018 | 29.5524 | 29.5524 | 29.5524 | 29.1316 | 29.2008 | 29.1916 | 29.1916 | 29.1916 | 29.1916 | 29.1916 | 29.1916 | 29.1916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.7552 | 44.7683 | 29.2243 | 29.2842 | 29.0018 | 29.5524 | 29.1316 | 29.2008 | 29.1916
|  |  |  | CARU3A_CHAPX1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38434 | 0.38434 | 0.38434 | 0.39013 | 0.38945 | 0.39186 | 0.39186 | 0.39186 | 0.39186 | 0.39186 | 0.39186 | 0.39186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38434 | 0.39013 | 0.38945 | 0.39186
|  |  | ANANT2_CHAP3-_1 | ANANT2_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.7633 | 44.7707 | 44.7707 | 29.2247 | 29.2846 | 29.0021 | 29.0021 | 29.5527 | 29.5527 | 29.5527 | 29.132 | 29.2012 | 28.9093 | 28.9093 | 28.9093 | 28.9093 | 28.9093 | 28.9093 | 28.9093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.7633 | 44.7707 | 29.2247 | 29.2846 | 29.0021 | 29.5527 | 29.132 | 29.2012 | 28.9093
|  |  | EWEH3-_MIBI3-_1 | EWHC3-_MIBI3-_1 | 0 | 0 | 0 | 0 | 3.7669 | 3.7669 | 3.7669 | 3.7669 | 3.7524 | 3.7669 | 3.7669 | 3.7669 | 3.7524 | 3.7524 | 3.7524 | 3.7524 | 3.7524 | 3.9074 | 3.9074 | 3.987 | 3.987 | 4.04 | 3.9752 | 3.8986 | 3.8986 | 26.6807 | 26.6807 | 26.6807 | 25.016 | 25.8453 | 23.0246 | 23.0246 | 23.0246 | 23.0246 | 23.0246 | 23.0246 | 23.0246 | 0 | 0 | 0 | 0 | 3.7829 | 3.7669 | 3.7524 | 3.9074 | 3.987 | 4.04 | 3.9752 | 3.8986 | 26.6807 | 25.016 | 25.8453 | 23.0246
|  |  |  | CRAG5A_LAHO5-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53212 | 0.58964 | 0.6023 | 0.6023 | 0.60028 | 0.60028 | 0.60028 | 0.60163 | 0.6004 | 0.60012 | 0.60012 | 0.60012 | 0.60012 | 0.60012 | 0.60012 | 0.60012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53212 | 0.58964 | 0.6023 | 0.60028 | 0.60163 | 0.6004 | 0.60012
|  |  | CHAPX4_LOBI3A_1 | CHAPX4_LOBI3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5875 | 52.3481 | 31.2536 | 31.2536 | 31.2536 | 31.2536 | 31.2536 | 31.2536 | 31.2536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5875 | 52.3481 | 31.2536
|  |  | CHAPX1_LOBI3A_1 | CHAPX1_LOBI3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.7871 | 65.7871 | 65.7871 | 63.8599 | 54.9076 | 44.4463 | 44.4463 | 44.4463 | 44.4463 | 44.4463 | 44.4463 | 44.4463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.7871 | 63.8599 | 54.9076 | 44.4463
|  |  | CHAP3-_GRNA3B_1 | CHAP3-_GRNA3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.526 | 44.8233 | 44.8233 | 30.0403 | 30.0403 | 30.0403 | 29.5986 | 29.6718 | 19.7967 | 19.7967 | 19.7967 | 19.7967 | 19.7967 | 19.7967 | 19.7967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.526 | 44.8233 | 30.0403 | 29.5986 | 29.6718 | 19.7967
|  |  | CHAP3-_MINS3-_1 | CHAP3-_MINS3-_1 | 0 | 0 | 0 | 0 | 6.804 | 6.804 | 6.804 | 6.7688 | 6.7426 | 6.7688 | 6.7688 | 6.7688 | 6.7426 | 6.7426 | 6.7426 | 6.7426 | 6.7426 | 7.0216 | 7.0216 | 7.0499 | 7.0499 | 49.2415 | 49.72 | 47.9819 | 47.9819 | 52.5142 | 52.5142 | 52.5142 | 48.6143 | 49.0691 | 48.1835 | 48.1835 | 48.1835 | 48.1835 | 48.1835 | 48.1835 | 48.1835 | 0 | 0 | 0 | 6.804 | 6.7976 | 6.7688 | 6.7426 | 7.0216 | 7.0499 | 49.2415 | 49.72 | 47.9819 | 52.5142 | 48.6143 | 49.0691 | 48.1835
|  |  | CHAP3-_STCR3-_1 | CHAP3-_STCR3-_1 | 0 | 0 | 0 | 0 | 3.2408 | 2.8017 | 2.8017 | 3.6839 | 4.2787 | 3.6839 | 3.6839 | 3.6839 | 4.2787 | 4.2787 | 4.2787 | 4.2787 | 4.2787 | 16.3602 | 16.3602 | 19.3054 | 19.3054 | 11.1399 | 15.9203 | 12.5263 | 12.5263 | 26.1824 | 26.1824 | 26.1824 | 21.0287 | 22.7633 | 19.677 | 19.677 | 19.677 | 19.677 | 19.677 | 19.677 | 19.677 | 0 | 3.2408 | 3.2408 | 2.8017 | 3.0557 | 3.6839 | 4.2787 | 16.3602 | 19.3054 | 11.1399 | 15.9203 | 12.5263 | 26.1824 | 21.0287 | 22.7633 | 19.677
|  |  | LOBI3B_LOBIT2_1 | LOBI3B_LOBIT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6348 | 0.76038 | 0.77571 | 0.81002 | 0.81002 | 0.81002 | 0.81002 | 0.81002 | 0.81002 | 0.81002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6348 | 0.76038 | 0.77571 | 0.81002
|  |  |  | lne_AL048A_GRNA1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25431 | 0.89565 | 0.25431 | 0.25431 | 0.25431 | 0.89565 | 0.89565 | 0.89565 | 0.89565 | 0.89565 | 0.70492 | 0.70492 | 0.70214 | 0.70214 | 0.71461 | 0.71316 | 0.88967 | 0.88967 | 0.70672 | 0.70672 | 0.70672 | 0.88572 | 0.71518 | 0.88817 | 0.88817 | 0.88817 | 0.88817 | 0.88817 | 0.88817 | 0.88817 | 0 | 0 | 0 | 0 | 0 | 0.25431 | 0.89565 | 0.70492 | 0.70214 | 0.71461 | 0.71316 | 0.88967 | 0.70672 | 0.88572 | 0.71518 | 0.88817
|  |  | CHAP1-_AL048A_1 | lne_CHAP1-_AL048A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76331 | 1.4655 | 0.76331 | 0.76331 | 0.76331 | 1.4655 | 1.4655 | 1.4655 | 1.4655 | 1.4655 | 1.1502 | 1.1502 | 1.1456 | 1.1456 | 1.166 | 1.1636 | 1.4502 | 1.4502 | 1.1531 | 1.1531 | 1.1531 | 1.4438 | 1.1669 | 1.4478 | 1.4478 | 1.4478 | 1.4478 | 1.4478 | 1.4478 | 1.4478 | 0 | 0 | 0 | 0 | 0 | 0.76331 | 1.4655 | 1.1502 | 1.1456 | 1.166 | 1.1636 | 1.4502 | 1.1531 | 1.4438 | 1.1669 | 1.4478
|  |  |  | lne_AL048B_GRNA1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003152 | 0.0031727 | 0.003152 | 0.003152 | 0.003152 | 0.0031727 | 0.0031727 | 0.0031727 | 0.0031727 | 0.0031727 | 0.0024754 | 0.0024754 | 0.0024656 | 0.0024656 | 0.0025094 | 0.0025043 | 0.0031142 | 0.0031142 | 0.0024817 | 0.0024817 | 0.0024817 | 0.0031004 | 0.0025114 | 0.003109 | 0.003109 | 0.003109 | 0.003109 | 0.003109 | 0.003109 | 0.003109 | 0 | 0 | 0 | 0 | 0 | 0.003152 | 0.0031727 | 0.0024754 | 0.0024656 | 0.0025094 | 0.0025043 | 0.0031142 | 0.0024817 | 0.0031004 | 0.0025114 | 0.003109
|  |  |  | lne_CHAP1-_AL048B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034395 | 0.003462 | 0.0034395 | 0.0034395 | 0.0034395 | 0.003462 | 0.003462 | 0.003462 | 0.003462 | 0.003462 | 0.0027011 | 0.0027011 | 0.0026904 | 0.0026904 | 0.0027382 | 0.0027327 | 0.0033982 | 0.0033982 | 0.002708 | 0.002708 | 0.002708 | 0.0033832 | 0.0027404 | 0.0033925 | 0.0033925 | 0.0033925 | 0.0033925 | 0.0033925 | 0.0033925 | 0.0033925 | 0 | 0 | 0 | 0 | 0 | 0.0034395 | 0.003462 | 0.0027011 | 0.0026904 | 0.0027382 | 0.0027327 | 0.0033982 | 0.002708 | 0.0033832 | 0.0027404 | 0.0033925
|  |  |  | CHAP08_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | CHAP3-_SOLWAY | CHAP3-_SOLWAY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | CHAP3A1 | CHAP3A1 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | CHAP3A2 | CHAP3A2 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | CHAP1-_CHAP3-_1 | CHAP1-_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.2953 | 13.2953 | 13.2953 | 13.8748 | 13.8748 | 13.8748 | 13.8748 | 13.8748 | 85.8965 | 145.6598 | 170.5142 | 170.5142 | 238.7913 | 267.1959 | 224.1193 | 224.1193 | 273.5382 | 273.5382 | 273.5382 | 259.8641 | 253.8772 | 215.1404 | 215.1404 | 215.1404 | 215.1404 | 215.1404 | 215.1404 | 215.1404 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | CHAP1-_CHAP3-_2 | CHAP1-_CHAP3-_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | CHAP1-_M1-_1 | CHAP1-_M1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.2953 | 13.2953 | 13.8748 | 13.8748 | 13.8748 | 13.8748 | 13.8748 | 85.8965 | 145.6598 | 170.5142 | 170.5142 | 238.7913 | 267.1959 | 224.1193 | 224.1193 | 273.5382 | 273.5382 | 273.5382 | 259.8641 | 253.8772 | 215.1404 | 215.1404 | 215.1404 | 215.1404 | 215.1404 | 215.1404 | 215.1404 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | CHAP1-_M1-_2 | CHAP1-_M1-_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | CHAP1-_R1-_1 | CHAP1-_R1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | HARK | HARK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | DUMF-2 | DUMF-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ECCF-2 | ECCF-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | GRNA-2 | GRNA-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | DUMF-1 | DUMF-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ECCF-1 | ECCF-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | CHAP1-_T1 | CHAP1-_T1 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | CHAP1-_T2 | CHAP1-_T2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | GRNA-1 | GRNA-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | STCR3- | STCR3- | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | STCR3-_STCR0G | STCR3-_STCR0G | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | STCR0G-_2 | STCR0G-_2 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | STCR0G-_1 | STCR0G-_1 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | STRC0G-_STCRLVT | STRC0G-_STCRLVT | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | STCR_AUX | STCR_AUX | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | STCR_DIESEL | STCR_DIESEL | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | MINS3- | MINS3- | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | MINS3-_MINSC | MINS3-_MINSC | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | MINS0G | MINS0G | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | EWEH3- | EWEH3- | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | EWEH3-_EWEH0G_1 | EWHC3-_EWHC0G_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | EWEH0G | EWEH0G | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | GRNA1-_SGT1 | GRNA1-_SGT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | GRNA1-_SGT2 | GRNA1-_SGT2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | GRNA1-_EWEH | GRNA1-_EWEH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | GRNA4-_M1-_SGT1 | GRNA4-_M1-_SGT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 80 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | CHAP1-_GRNA1 | CHAP1-_GRNA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | EWEH3 | EWEH3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | EWEH3-_GRID1A-_WG2 | EWEH3-_GRID1A-_WG2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | EWEH0G_2 | EWEH0G_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | HARK4 | HARK4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.01 | 0.01
|  |  | GRNA4-_M1 | GRNA4-_M1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01
|  |  | CHAP2-_GRNA1 | CHAP2-_GRNA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | HAWI | CHAP2-_GRNA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
End of sheet
Lines are on SLD
Not used in simulation
Vlookup
Note on D9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 132kV line to Harker
Note on D15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: section of line from Chapelcross to T-off to Dumfries sector 414
Note on D21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Langholm 33kV A to Langholm T1
Note on D22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Langholm 33kV B to Langholm T2
Note on D29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Section of line between Chapelcross and Lockerbie going to Dumfries Sector 414
Note on D39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable section of 132kV line A from Chapelcross 132kV to Getna
Note on D40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable section of 132kV line A from Chapelcross 132kV to Getna
Note on D41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable section of 132kV line B from Chapelcross 132kV to Getna
Note on D42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Overhead line B from Chapelcross 132kV to Getna
Note on D43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Gretna 33kV to T junction of line from Chapelcross to Langholm
Note on E43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Values beyond this point need to be calculated

## Lines - Current
Lines - Current
Results
Lines
|  |  |  | Name in Simulation SLD |  |  | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[7 empty] | Current (kA) >>> | [36 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  | network | Name |  | Rating (kA) | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  | 0 |  | lne_CHAP1-_HAKB1-_1 | 0.57735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  | CRAG5B_LAHO5-_1 | 0.27293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0155e-09 | 1.1277e-09 | 1.1523e-09 | 1.1523e-09 | 1.1484e-09 | 1.1484e-09 | 1.1484e-09 | 1.151e-09 | 1.1486e-09 | 1.1481e-09 | 1.1481e-09 | 1.1481e-09 | 1.1481e-09 | 1.1481e-09 | 1.1481e-09 | 1.1481e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0155e-09 | 1.1277e-09 | 1.1523e-09 | 1.1484e-09 | 1.151e-09 | 1.1486e-09 | 1.1481e-09
|  |  | 0 | CHAPX3_LAHO3B_1 | CHAPX3_LAHO3B_1 | 0.42799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038678 | 0.038678 | 0.019474 | 0.019474 | 0.019474 | 0.019193 | 0.019239 | 0.06279 | 0.06279 | 0.06279 | 0.06279 | 0.06279 | 0.06279 | 0.06279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038678 | 0.019474 | 0.019193 | 0.019239 | 0.06279
|  |  | 0 | LOBI3B_MOFTT2_1 | LOBI3B_MOFTT2_1 | 0.19402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.084131 | 0.045672 | 0.045672 | 0.045672 | 0.045672 | 0.045672 | 0.045672 | 0.045672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.084131 | 0.045672
|  |  | 0 |  | lne_CHAP1-_DUMF1-_1 | 0.74793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | CHAP3-_LOBI3B_1 | CHAP3-_LOBI3B_1 | 0.36496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28574 | 0.1329 | 0.2195 | 0.1831 | 0.1831 | 0.1831 | 0.1831 | 0.1831 | 0.1831 | 0.1831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28574 | 0.1329 | 0.2195 | 0.1831
|  |  | 0 |  | CHAP3-_CHAPX1_1 | 0.43091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28313 | 0.28313 | 0.28313 | 0.275 | 0.23646 | 0.19159 | 0.19159 | 0.19159 | 0.19159 | 0.19159 | 0.19159 | 0.19159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28313 | 0.275 | 0.23646 | 0.19159
|  |  | 0 | CHAPX4_KIBAT1_1 | CHAPX4_KIBAT1_1 | 0.31107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053952 | 0.039642 | 0.025692 | 0.025692 | 0.025692 | 0.025692 | 0.025692 | 0.025692 | 0.025692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053952 | 0.039642 | 0.025692
|  |  | 0 | CHAPX4_MOFTT1_1 | CHAPX4_MOFTT1_1 | 0.31107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085367 | 0.062134 | 0.036021 | 0.036021 | 0.036021 | 0.036021 | 0.036021 | 0.036021 | 0.036021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085367 | 0.062134 | 0.036021
|  |  | 0 | CHAP3-_CHAPX3_1 | CHAP3-_CHAPX3_1 | 0.43091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039017 | 0.039017 | 0.020864 | 0.020864 | 0.020864 | 0.020656 | 0.02069 | 0.1058 | 0.1058 | 0.1058 | 0.1058 | 0.1058 | 0.1058 | 0.1058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039017 | 0.020864 | 0.020656 | 0.02069 | 0.1058
|  |  | 0 | GRNA3A_GRNAT1_1 | GRNA3A_GRNAT1_1 | 17.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017478 | 0.0017478 | 0.0017478 | 0.0017478 | 0.0017478 | 0.0017478 | 0.0017478 | 0.0017478 | 0.0017478 | 0.0017478 | 0.0017478 | 0.041839 | 0.041839 | 0.041839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00013087 | 0.00012901 | 0.00013088 | 0.00013057 | 0.041839
|  |  | 0 | LOBI3A_LOBIT1_1 | LOBI3A_LOBIT1_1 | 17.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28349 | 0.28349 | 0.28349 | 0.13649 | 0.13548 | 0.13107 | 0.13107 | 0.13107 | 0.13107 | 0.13107 | 0.13107 | 0.13107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28349 | 0.13649 | 0.13548 | 0.13107
|  |  | 0 |  | LAHO3A_LAHOT1_1 | 17.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28993 | 0.19627 | 0.12139 | 0.12139 | 0.1218 | 0.1218 | 0.1218 | 0.11995 | 0.12019 | 0.07447 | 0.07447 | 0.07447 | 0.07447 | 0.07447 | 0.07447 | 0.07447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28993 | 0.19627 | 0.12139 | 0.1218 | 0.11995 | 0.12019 | 0.07447
|  |  | 0 |  | LAHO3B_LAHOT2_1 | 17.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8806e-10 | 3.8806e-10 | 3.8824e-10 | 3.8824e-10 | 3.8824e-10 | 3.888e-10 | 3.8788e-10 | 0.043644 | 0.043644 | 0.043644 | 0.043644 | 0.043644 | 0.043644 | 0.043644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8806e-10 | 3.8824e-10 | 3.888e-10 | 3.8788e-10 | 0.043644
|  |  | 0 | MIBI3-_MIBIT1_1 | MIBI3-_MIBIT1_1 | 17.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19027 | 0.19027 | 0.1444 | 0.094675 | 0.092869 | 0.092869 | 0.093132 | 0.093132 | 0.093132 | 0.0919 | 0.092059 | 0.091484 | 0.091484 | 0.091484 | 0.091484 | 0.091484 | 0.091484 | 0.091484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19027 | 0.1444 | 0.094675 | 0.092869 | 0.093132 | 0.0919 | 0.092059 | 0.091484
|  |  | 0 | GRNA3B_GRNAT2_1 | GRNA3B_GRNAT2_1 | 17.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26518 | 0.19319 | 0.19319 | 0.12947 | 0.12947 | 0.12947 | 0.12757 | 0.12789 | 0.085324 | 0.085324 | 0.085324 | 0.085324 | 0.085324 | 0.085324 | 0.085324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26518 | 0.19319 | 0.12947 | 0.12757 | 0.12789 | 0.085324
|  |  | 0 | MIBI3-_LAHO3A_1 | MIBI3-_LAHO3A_1 | 0.19402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28993 | 0.19627 | 0.12139 | 0.12139 | 0.1218 | 0.1218 | 0.1218 | 0.11995 | 0.12019 | 0.07447 | 0.07447 | 0.07447 | 0.07447 | 0.07447 | 0.07447 | 0.07447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28993 | 0.19627 | 0.12139 | 0.1218 | 0.11995 | 0.12019 | 0.07447
|  |  | 0 | LAHO3B_NEWCT1_1 | LAHO3B_NEWCT1_1 | 0.42799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038752 | 0.038752 | 0.019516 | 0.019516 | 0.019516 | 0.019235 | 0.019281 | 0.019456 | 0.019456 | 0.019456 | 0.019456 | 0.019456 | 0.019456 | 0.019456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038752 | 0.019516 | 0.019235 | 0.019281 | 0.019456
|  |  | 0 | CHAP3-_MIBI3-_1 | CHAP3-_MIBI3-_1 | 0.36496 | 0 | 0 | 0 | 0 | 0.010374 | 0.010374 | 0.010374 | 0.010374 | 0.010414 | 0.010374 | 0.010374 | 0.010374 | 0.010414 | 0.010414 | 0.010414 | 0.010414 | 0.010414 | 0.010071 | 0.010071 | 0.19934 | 0.19934 | 0.4378 | 0.2973 | 0.22183 | 0.22183 | 0.14565 | 0.14565 | 0.14565 | 0.1405 | 0.14256 | 0.091005 | 0.091005 | 0.091005 | 0.091005 | 0.091005 | 0.091005 | 0.091005 | 0 | 0 | 0 | 0 | 0.010332 | 0.010374 | 0.010414 | 0.010071 | 0.19934 | 0.4378 | 0.2973 | 0.22183 | 0.14565 | 0.1405 | 0.14256 | 0.091005
|  |  | 0 | ANANT1_CHAP3-_1 | ANANT1_CHAP3-_1 | 0.36496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21808 | 0.21808 | 0.16338 | 0.16338 | 0.10666 | 0.10687 | 0.10584 | 0.10584 | 0.10785 | 0.10785 | 0.10785 | 0.10632 | 0.10657 | 0.10654 | 0.10654 | 0.10654 | 0.10654 | 0.10654 | 0.10654 | 0.10654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21808 | 0.16338 | 0.10666 | 0.10687 | 0.10584 | 0.10785 | 0.10632 | 0.10657 | 0.10654
|  |  | 0 |  | CARU3A_CHAPX1_1 | 0.43091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016562 | 0.0016562 | 0.0016562 | 0.0016811 | 0.0016782 | 0.0016886 | 0.0016886 | 0.0016886 | 0.0016886 | 0.0016886 | 0.0016886 | 0.0016886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016562 | 0.0016811 | 0.0016782 | 0.0016886
|  |  | 0 | ANANT2_CHAP3-_1 | ANANT2_CHAP3-_1 | 0.36496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21811 | 0.16339 | 0.16339 | 0.10666 | 0.10688 | 0.10584 | 0.10584 | 0.10785 | 0.10785 | 0.10785 | 0.10632 | 0.10657 | 0.10551 | 0.10551 | 0.10551 | 0.10551 | 0.10551 | 0.10551 | 0.10551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21811 | 0.16339 | 0.10666 | 0.10688 | 0.10584 | 0.10785 | 0.10632 | 0.10657 | 0.10551
|  |  | 0 | EWEH3-_MIBI3-_1 | EWHC3-_MIBI3-_1 | 0.40065 | 0 | 0 | 0 | 0 | 0.015092 | 0.015092 | 0.015092 | 0.015092 | 0.015034 | 0.015092 | 0.015092 | 0.015092 | 0.015034 | 0.015034 | 0.015034 | 0.015034 | 0.015034 | 0.015655 | 0.015655 | 0.015974 | 0.015974 | 0.016186 | 0.015927 | 0.01562 | 0.01562 | 0.1069 | 0.1069 | 0.1069 | 0.10023 | 0.10355 | 0.092247 | 0.092247 | 0.092247 | 0.092247 | 0.092247 | 0.092247 | 0.092247 | 0 | 0 | 0 | 0 | 0.015156 | 0.015092 | 0.015034 | 0.015655 | 0.015974 | 0.016186 | 0.015927 | 0.01562 | 0.1069 | 0.10023 | 0.10355 | 0.092247
|  |  | 0 |  | CRAG5A_LAHO5-_1 | 0.5616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029884 | 0.0033114 | 0.0033825 | 0.0033825 | 0.0033712 | 0.0033712 | 0.0033712 | 0.0033788 | 0.0033719 | 0.0033703 | 0.0033703 | 0.0033703 | 0.0033703 | 0.0033703 | 0.0033703 | 0.0033703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029884 | 0.0033114 | 0.0033825 | 0.0033712 | 0.0033788 | 0.0033719 | 0.0033703
|  |  | 0 | CHAPX4_LOBI3A_1 | CHAPX4_LOBI3A_1 | 0.19402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1389 | 0.10157 | 0.06064 | 0.06064 | 0.06064 | 0.06064 | 0.06064 | 0.06064 | 0.06064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1389 | 0.10157 | 0.06064
|  |  | 0 | CHAPX1_LOBI3A_1 | CHAPX1_LOBI3A_1 | 0.43091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28349 | 0.28349 | 0.28349 | 0.27518 | 0.2366 | 0.19153 | 0.19153 | 0.19153 | 0.19153 | 0.19153 | 0.19153 | 0.19153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28349 | 0.27518 | 0.2366 | 0.19153
|  |  | 0 | CHAP3-_GRNA3B_1 | CHAP3-_GRNA3B_1 | 0.431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26518 | 0.19319 | 0.19319 | 0.12947 | 0.12947 | 0.12947 | 0.12757 | 0.12789 | 0.085324 | 0.085324 | 0.085324 | 0.085324 | 0.085324 | 0.085324 | 0.085324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26518 | 0.19319 | 0.12947 | 0.12757 | 0.12789 | 0.085324
|  |  | 0 | CHAP3-_MINS3-_1 | CHAP3-_MINS3-_1 | 0.69982 | 0 | 0 | 0 | 0 | 0.047616 | 0.047616 | 0.047616 | 0.04737 | 0.047186 | 0.04737 | 0.04737 | 0.04737 | 0.047186 | 0.047186 | 0.047186 | 0.047186 | 0.047186 | 0.049138 | 0.049138 | 0.049337 | 0.049337 | 0.3446 | 0.34795 | 0.33579 | 0.33579 | 0.3675 | 0.3675 | 0.3675 | 0.34021 | 0.34339 | 0.3372 | 0.3372 | 0.3372 | 0.3372 | 0.3372 | 0.3372 | 0.3372 | 0 | 0 | 0 | 0.047616 | 0.047571 | 0.04737 | 0.047186 | 0.049138 | 0.049337 | 0.3446 | 0.34795 | 0.33579 | 0.3675 | 0.34021 | 0.34339 | 0.3372
|  |  | 0 | CHAP3-_STCR3-_1 | CHAP3-_STCR3-_1 | 2.7993 | 0 | 0 | 0 | 0 | 0.090719 | 0.078426 | 0.078426 | 0.10312 | 0.11977 | 0.10312 | 0.10312 | 0.10312 | 0.11977 | 0.11977 | 0.11977 | 0.11977 | 0.11977 | 0.45797 | 0.45797 | 0.54041 | 0.54041 | 0.31184 | 0.44565 | 0.35065 | 0.35065 | 0.73292 | 0.73292 | 0.73292 | 0.58865 | 0.63721 | 0.55081 | 0.55081 | 0.55081 | 0.55081 | 0.55081 | 0.55081 | 0.55081 | 0.090719 | 0 | 0.090719 | 0.078426 | 0.085538 | 0.10312 | 0.11977 | 0.45797 | 0.54041 | 0.31184 | 0.44565 | 0.35065 | 0.73292 | 0.58865 | 0.63721 | 0.55081
|  |  | 0 | LOBI3B_LOBIT2_1 | LOBI3B_LOBIT2_1 | 17.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28574 | 0.1329 | 0.13558 | 0.14158 | 0.14158 | 0.14158 | 0.14158 | 0.14158 | 0.14158 | 0.14158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28574 | 0.1329 | 0.13558 | 0.14158
|  |  | 0 |  | lne_AL048A_GRNA1-_1 | 0.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016021 | 0.0056426 | 0.0016021 | 0.0016021 | 0.0016021 | 0.0056426 | 0.0056426 | 0.0056426 | 0.0056426 | 0.0056426 | 0.004441 | 0.004441 | 0.0044235 | 0.0044235 | 0.004502 | 0.0044929 | 0.0056049 | 0.0056049 | 0.0044524 | 0.0044524 | 0.0044524 | 0.00558 | 0.0045056 | 0.0055955 | 0.0055955 | 0.0055955 | 0.0055955 | 0.0055955 | 0.0055955 | 0.0055955 | 0 | 0 | 0 | 0 | 0 | 0.0016021 | 0.0056426 | 0.004441 | 0.0044235 | 0.004502 | 0.0044929 | 0.0056049 | 0.0044524 | 0.00558 | 0.0045056 | 0.0055955
|  |  | 0 | CHAP1-_AL048A_1 | lne_CHAP1-_AL048A_1 | 0.57735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004407 | 0.0084609 | 0.004407 | 0.004407 | 0.004407 | 0.0084609 | 0.0084609 | 0.0084609 | 0.0084609 | 0.0084609 | 0.0066406 | 0.0066406 | 0.0066144 | 0.0066144 | 0.0067319 | 0.0067183 | 0.0083727 | 0.0083727 | 0.0066576 | 0.0066576 | 0.0066576 | 0.0083356 | 0.0067373 | 0.0083587 | 0.0083587 | 0.0083587 | 0.0083587 | 0.0083587 | 0.0083587 | 0.0083587 | 0 | 0 | 0 | 0 | 0 | 0.004407 | 0.0084609 | 0.0066406 | 0.0066144 | 0.0067319 | 0.0067183 | 0.0083727 | 0.0066576 | 0.0083356 | 0.0067373 | 0.0083587
|  |  | 0 |  | lne_AL048B_GRNA1-_1 | 0.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9858e-05 | 1.9988e-05 | 1.9858e-05 | 1.9858e-05 | 1.9858e-05 | 1.9988e-05 | 1.9988e-05 | 1.9988e-05 | 1.9988e-05 | 1.9988e-05 | 1.5595e-05 | 1.5595e-05 | 1.5533e-05 | 1.5533e-05 | 1.5809e-05 | 1.5777e-05 | 1.9619e-05 | 1.9619e-05 | 1.5635e-05 | 1.5635e-05 | 1.5635e-05 | 1.9533e-05 | 1.5822e-05 | 1.9587e-05 | 1.9587e-05 | 1.9587e-05 | 1.9587e-05 | 1.9587e-05 | 1.9587e-05 | 1.9587e-05 | 0 | 0 | 0 | 0 | 0 | 1.9858e-05 | 1.9988e-05 | 1.5595e-05 | 1.5533e-05 | 1.5809e-05 | 1.5777e-05 | 1.9619e-05 | 1.5635e-05 | 1.9533e-05 | 1.5822e-05 | 1.9587e-05
|  |  | 0 |  | lne_CHAP1-_AL048B_1 | 0.5773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9856e-05 | 1.9986e-05 | 1.9856e-05 | 1.9856e-05 | 1.9856e-05 | 1.9986e-05 | 1.9986e-05 | 1.9986e-05 | 1.9986e-05 | 1.9986e-05 | 1.5593e-05 | 1.5593e-05 | 1.5532e-05 | 1.5532e-05 | 1.5808e-05 | 1.5776e-05 | 1.9618e-05 | 1.9618e-05 | 1.5633e-05 | 1.5633e-05 | 1.5633e-05 | 1.9531e-05 | 1.582e-05 | 1.9585e-05 | 1.9585e-05 | 1.9585e-05 | 1.9585e-05 | 1.9585e-05 | 1.9585e-05 | 1.9585e-05 | 0 | 0 | 0 | 0 | 0 | 1.9856e-05 | 1.9986e-05 | 1.5593e-05 | 1.5532e-05 | 1.5808e-05 | 1.5776e-05 | 1.9618e-05 | 1.5633e-05 | 1.9531e-05 | 1.582e-05 | 1.9585e-05
|  |  | 0 |  | CHAP08_CHAPX3_1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP3-_SOLWAY | CHAP3-_SOLWAY | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP3A1 | CHAP3A1 | 999 | 0 | 0 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP3A2 | CHAP3A2 | 999 | 0 | 0 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP1-_CHAP3-_1 | CHAP1-_CHAP3-_1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132.8198 | 132.8198 | 132.8198 | 138.6097 | 138.6097 | 138.6097 | 138.6097 | 138.6097 | 858.1063 | 1455.1412 | 1703.4369 | 1703.4369 | 2385.5255 | 2669.2868 | 2238.952 | 2238.952 | 2732.6464 | 2732.6464 | 2732.6464 | 2596.0427 | 2536.2333 | 2149.2522 | 2149.2522 | 2149.2522 | 2149.2522 | 2149.2522 | 2149.2522 | 2149.2522 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP1-_CHAP3-_2 | CHAP1-_CHAP3-_2 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP1-_M1-_1 | CHAP1-_M1-_1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132.8198 | 132.8198 | 138.6097 | 138.6097 | 138.6097 | 138.6097 | 138.6097 | 858.1063 | 1455.1412 | 1703.4369 | 1703.4369 | 2385.5255 | 2669.2868 | 2238.952 | 2238.952 | 2732.6464 | 2732.6464 | 2732.6464 | 2596.0427 | 2536.2333 | 2149.2522 | 2149.2522 | 2149.2522 | 2149.2522 | 2149.2522 | 2149.2522 | 2149.2522 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP1-_M1-_2 | CHAP1-_M1-_2 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP1-_R1-_1 | CHAP1-_R1-_1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | HARK | HARK | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | DUMF-2 | DUMF-2 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | ECCF-2 | ECCF-2 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA-2 | GRNA-2 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | DUMF-1 | DUMF-1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | ECCF-1 | ECCF-1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP1-_T1 | CHAP1-_T1 | 999 | 0 | 0 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP1-_T2 | CHAP1-_T2 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA-1 | GRNA-1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STCR3- | STCR3- | 999 | 0 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STCR3-_STCR0G | STCR3-_STCR0G | 999 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STCR0G-_2 | STCR0G-_2 | 999 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STCR0G-_1 | STCR0G-_1 | 999 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STRC0G-_STCRLVT | STRC0G-_STCRLVT | 999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STCR_AUX | STCR_AUX | 999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STCR_DIESEL | STCR_DIESEL | 999 | 0.0999 | 0.0999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | MINS3- | MINS3- | 999 | 0 | 0 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | MINS3-_MINSC | MINS3-_MINSC | 999 | 0 | 0 | 0 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | MINS0G | MINS0G | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | EWEH3- | EWEH3- | 999 | 0 | 0 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | EWEH3-_EWEH0G_1 | EWHC3-_EWHC0G_1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | EWEH0G | EWEH0G | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA1-_SGT1 | GRNA1-_SGT1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA1-_SGT2 | GRNA1-_SGT2 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA1-_EWEH | GRNA1-_EWEH | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA4-_M1-_SGT1 | GRNA4-_M1-_SGT1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 799.2 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP1-_GRNA1 | CHAP1-_GRNA1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | EWEH3 | EWEH3 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | EWEH3-_GRID1A-_WG2 | EWEH3-_GRID1A-_WG2 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | EWEH0G_2 | EWEH0G_2 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | HARK4 | HARK4 | 3.1899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0031899 | 0.00031899 | 0.00031899 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA4-_M1 | GRNA4-_M1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0999 | 0.0999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP2-_GRNA1 | CHAP2-_GRNA1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | HAWI | CHAP2-_GRNA1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
Lines are on SLD
Not used in simulation
Vlookup
Note on E9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 132kV line to Harker
Note on E15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: section of line from Chapelcross to T-off to Dumfries sector 414
Note on E21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Langholm 33kV A to Langholm T1
Note on E22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Langholm 33kV B to Langholm T2
Note on E29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Section of line between Chapelcross and Lockerbie going to Dumfries Sector 414
Note on E39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable section of 132kV line A from Chapelcross 132kV to Getna
Note on E40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable section of 132kV line A from Chapelcross 132kV to Getna
Note on E41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable section of 132kV line B from Chapelcross 132kV to Getna
Note on E42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Overhead line B from Chapelcross 132kV to Getna
Note on E43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Gretna 33kV to T junction of line from Chapelcross to Langholm

## Lines - Reactive Power
Lines - Reactive Power
Results
Lines
|  |  |  | Name in Simulation SLD |  | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[6 empty] | Reactive Power >>> | [36 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  | network | Name | PF Name | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  | 0 |  | lne_CHAP1-_HAKB1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  | CRAG5B_LAHO5-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2218e-15 | -1.1451e-14 | 3.244e-15 | 3.244e-15 | 1.3082e-14 | 1.3082e-14 | 1.3082e-14 | 2.6283e-14 | 1.0918e-14 | -8.384e-14 | -8.384e-14 | -8.384e-14 | -8.384e-14 | -8.384e-14 | -8.384e-14 | -8.384e-14 | -8.384e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2218e-15 | -1.1451e-14 | 3.244e-15 | 1.3082e-14 | 2.6283e-14 | 1.0918e-14 | -8.384e-14
|  |  | 0 | CHAPX3_LAHO3B_1 | CHAPX3_LAHO3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.123 | 0.123 | -0.0061391 | -0.0061391 | -0.0061391 | -0.0089177 | -0.0083695 | -0.48324 | -0.48324 | -0.48324 | -0.48324 | -0.48324 | -0.48324 | -0.48324 | -0.48324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.123 | -0.0061391 | -0.0089177 | -0.0083695 | -0.48324
|  |  | 0 | LOBI3B_MOFTT2_1 | LOBI3B_MOFTT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067022 | -0.53678 | -0.53678 | -0.53678 | -0.53678 | -0.53678 | -0.53678 | -0.53678 | -0.53678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067022 | -0.53678
|  |  | 0 |  | lne_CHAP1-_DUMF1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | CHAP3-_LOBI3B_1 | CHAP3-_LOBI3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9445 | 3.9445 | 3.9445 | 0.88277 | 1.4771 | 2.103 | 2.103 | 2.103 | 2.103 | 2.103 | 2.103 | 2.103 | 2.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9445 | 0.88277 | 1.4771 | 2.103
|  |  | 0 |  | CHAP3-_CHAPX1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4766 | 3.4766 | 3.4766 | 1.7563 | 1.1473 | -0.43517 | -0.43517 | -0.43517 | -0.43517 | -0.43517 | -0.43517 | -0.43517 | -0.43517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4766 | 1.7563 | 1.1473 | -0.43517
|  |  | 0 | CHAPX4_KIBAT1_1 | CHAPX4_KIBAT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.31997 | -0.31265 | -0.29028 | -0.29028 | -0.29028 | -0.29028 | -0.29028 | -0.29028 | -0.29028 | -0.29028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.31997 | -0.31265 | -0.29028
|  |  | 0 | CHAPX4_MOFTT1_1 | CHAPX4_MOFTT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22308 | 0.083971 | 0.34243 | 0.34243 | 0.34243 | 0.34243 | 0.34243 | 0.34243 | 0.34243 | 0.34243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22308 | 0.083971 | 0.34243
|  |  | 0 | CHAP3-_CHAPX3_1 | CHAP3-_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043098 | 0.043098 | 0.16756 | 0.16756 | 0.16756 | 0.17505 | 0.17371 | 0.98008 | 0.98008 | 0.98008 | 0.98008 | 0.98008 | 0.98008 | 0.98008 | 0.98008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043098 | 0.16756 | 0.17505 | 0.17371 | 0.98008
|  |  | 0 | GRNA3A_GRNAT1_1 | GRNA3A_GRNAT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.0565e-11 | -7.0565e-11 | 1.7533e-11 | 1.7533e-11 | 1.7533e-11 | 3.2106e-11 | 1.8757e-10 | -0.35914 | -0.35914 | -0.35914 | -0.35914 | -0.35914 | -0.35914 | -0.35914 | -0.35914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.0565e-11 | 1.7533e-11 | 3.2106e-11 | 1.8757e-10 | -0.35914
|  |  | 0 | LOBI3A_LOBIT1_1 | LOBI3A_LOBIT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1248 | 2.1248 | 2.1248 | 0.53449 | 0.52659 | -0.89704 | -0.89704 | -0.89704 | -0.89704 | -0.89704 | -0.89704 | -0.89704 | -0.89704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1248 | 0.53449 | 0.52659 | -0.89704
|  |  | 0 |  | LAHO3A_LAHOT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1346 | 1.6125 | 0.78213 | 0.78213 | 0.78577 | 0.78577 | 0.78577 | 0.78333 | 0.78556 | 1.0719 | 1.0719 | 1.0719 | 1.0719 | 1.0719 | 1.0719 | 1.0719 | 1.0719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1346 | 1.6125 | 0.78213 | 0.78577 | 0.78333 | 0.78556 | 1.0719
|  |  | 0 |  | LAHO3B_LAHOT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.16e-14 | 1.16e-14 | 2.095e-14 | 2.095e-14 | 2.095e-14 | 8.0745e-16 | 6.7202e-15 | -0.50598 | -0.50598 | -0.50598 | -0.50598 | -0.50598 | -0.50598 | -0.50598 | -0.50598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.16e-14 | 2.095e-14 | 8.0745e-16 | 6.7202e-15 | -0.50598
|  |  | 0 | MIBI3-_MIBIT1_1 | MIBI3-_MIBIT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13642 | -0.08816 | -0.20095 | -0.20455 | -0.20455 | -0.20299 | -0.20299 | -0.20299 | -0.2034 | -0.20244 | -0.20589 | -0.20589 | -0.20589 | -0.20589 | -0.20589 | -0.20589 | -0.20589 | -0.20589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13642 | -0.08816 | -0.20095 | -0.20455 | -0.20299 | -0.2034 | -0.20244 | -0.20589
|  |  | 0 | GRNA3B_GRNAT2_1 | GRNA3B_GRNAT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2979 | 0.49516 | 0.49516 | 0.027883 | 0.027883 | 0.027883 | 0.024716 | 0.02779 | 0.10821 | 0.10821 | 0.10821 | 0.10821 | 0.10821 | 0.10821 | 0.10821 | 0.10821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2979 | 0.49516 | 0.027883 | 0.024716 | 0.02779 | 0.10821
|  |  | 0 | MIBI3-_LAHO3A_1 | MIBI3-_LAHO3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7541 | 2.3547 | 1.066 | 1.066 | 1.0716 | 1.0716 | 1.0716 | 1.0605 | 1.0639 | 1.1787 | 1.1787 | 1.1787 | 1.1787 | 1.1787 | 1.1787 | 1.1787 | 1.1787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7541 | 2.3547 | 1.066 | 1.0716 | 1.0605 | 1.0639 | 1.1787
|  |  | 0 | LAHO3B_NEWCT1_1 | LAHO3B_NEWCT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14065 | 0.14065 | 0.019994 | 0.019994 | 0.019994 | 0.018161 | 0.018552 | 0.019505 | 0.019505 | 0.019505 | 0.019505 | 0.019505 | 0.019505 | 0.019505 | 0.019505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14065 | 0.019994 | 0.018161 | 0.018552 | 0.019505
|  |  | 0 | CHAP3-_MIBI3-_1 | CHAP3-_MIBI3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.33026 | -0.33026 | -0.33917 | -0.33917 | -0.33917 | -0.34741 | -0.34741 | -0.34741 | -0.34741 | -0.34741 | -0.2644 | -0.2644 | 0.21168 | 5.9188 | 2.5926 | 0.96526 | 0.96526 | -3.013 | -3.013 | -3.013 | -2.5674 | -2.8418 | -1.7897 | -1.7897 | -1.7897 | -1.7897 | -1.7897 | -1.7897 | -1.7897 | -1.7897 | 0 | 0 | 0 | 0 | -0.33026 | -0.33917 | -0.34741 | -0.2644 | 0.21168 | 5.9188 | 2.5926 | 0.96526 | -3.013 | -2.5674 | -2.8418 | -1.7897
|  |  | 0 | ANANT1_CHAP3-_1 | ANANT1_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85345 | 0.85345 | 0.28164 | -0.048318 | -0.046358 | -0.055567 | -0.055567 | -0.048326 | -0.048326 | -0.048326 | -0.051345 | -0.049086 | -0.053834 | -0.053834 | -0.053834 | -0.053834 | -0.053834 | -0.053834 | -0.053834 | -0.053834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85345 | 0.28164 | -0.048318 | -0.046358 | -0.055567 | -0.048326 | -0.051345 | -0.049086 | -0.053834
|  |  | 0 |  | CARU3A_CHAPX1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0635e-14 | -1.0635e-14 | -1.0635e-14 | -2.0492e-14 | -6.2382e-15 | -5.4715e-15 | -5.4715e-15 | -5.4715e-15 | -5.4715e-15 | -5.4715e-15 | -5.4715e-15 | -5.4715e-15 | -5.4715e-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0635e-14 | -2.0492e-14 | -6.2382e-15 | -5.4715e-15
|  |  | 0 | ANANT2_CHAP3-_1 | ANANT2_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87076 | 0.87076 | 0.2904 | -0.045404 | -0.043417 | -0.052751 | -0.052751 | -0.045425 | -0.045425 | -0.045425 | -0.048472 | -0.046182 | -0.051335 | -0.051335 | -0.051335 | -0.051335 | -0.051335 | -0.051335 | -0.051335 | -0.051335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87076 | 0.2904 | -0.045404 | -0.043417 | -0.052751 | -0.045425 | -0.048472 | -0.046182 | -0.051335
|  |  | 0 | EWEH3-_MIBI3-_1 | EWHC3-_MIBI3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.33107 | -0.33107 | -0.33999 | -0.33999 | -0.33999 | -0.34823 | -0.34823 | -0.34823 | -0.34823 | -0.34823 | -0.26517 | -0.26517 | -0.22625 | -0.20159 | -0.23185 | -0.26962 | -0.26962 | -4.0425 | -4.0425 | -4.0425 | -3.5743 | -3.8575 | -2.8254 | -2.8254 | -2.8254 | -2.8254 | -2.8254 | -2.8254 | -2.8254 | -2.8254 | 0 | 0 | 0 | 0 | -0.33107 | -0.33999 | -0.34823 | -0.26517 | -0.22625 | -0.20159 | -0.23185 | -0.26962 | -4.0425 | -3.5743 | -3.8575 | -2.8254
|  |  | 0 |  | CRAG5A_LAHO5-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.991e-13 | -5.624e-13 | -3.9107e-13 | -3.9107e-13 | -1.4209e-12 | -1.4209e-12 | -1.4209e-12 | 3.2081e-13 | -2.3989e-12 | 6.8414e-12 | 6.8414e-12 | 6.8414e-12 | 6.8414e-12 | 6.8414e-12 | 6.8414e-12 | 6.8414e-12 | 6.8414e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.991e-13 | -5.624e-13 | -3.9107e-13 | -1.4209e-12 | 3.2081e-13 | -2.3989e-12 | 6.8414e-12
|  |  | 0 | CHAPX4_LOBI3A_1 | CHAPX4_LOBI3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.096888 | 0.22868 | -0.052149 | -0.052149 | -0.052149 | -0.052149 | -0.052149 | -0.052149 | -0.052149 | -0.052149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.096888 | 0.22868 | -0.052149
|  |  | 0 | CHAPX1_LOBI3A_1 | CHAPX1_LOBI3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4807 | 3.4807 | 3.4807 | 1.7682 | 1.1808 | -0.37923 | -0.37923 | -0.37923 | -0.37923 | -0.37923 | -0.37923 | -0.37923 | -0.37923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4807 | 1.7682 | 1.1808 | -0.37923
|  |  | 0 | CHAP3-_GRNA3B_1 | CHAP3-_GRNA3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2116 | 0.95561 | 0.95561 | 0.20825 | 0.20825 | 0.20825 | 0.19694 | 0.20136 | 0.15669 | 0.15669 | 0.15669 | 0.15669 | 0.15669 | 0.15669 | 0.15669 | 0.15669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2116 | 0.95561 | 0.20825 | 0.19694 | 0.20136 | 0.15669
|  |  | 0 | CHAP3-_MINS3-_1 | CHAP3-_MINS3-_1 | 0 | 0 | 0 | 0 | 0 | 0.72548 | 0.72548 | 0.72169 | 0.72169 | 0.70477 | 0.70477 | 0.70477 | 0.68914 | 0.68914 | 0.68914 | 0.68914 | 0.68914 | 0.84673 | 0.84673 | 0.8617 | -4.0201 | -4.7194 | -1.371 | -1.371 | -7.7954 | -7.7954 | -7.7954 | -2.9262 | -3.7439 | -1.9552 | -1.9552 | -1.9552 | -1.9552 | -1.9552 | -1.9552 | -1.9552 | -1.9552 | 0 | 0 | 0 | 0.72548 | 0.72169 | 0.70477 | 0.68914 | 0.84673 | 0.8617 | -4.0201 | -4.7194 | -1.371 | -7.7954 | -2.9262 | -3.7439 | -1.9552
|  |  | 0 | CHAP3-_STCR3-_1 | CHAP3-_STCR3-_1 | 0 | 0 | 5.4094e-14 | 5.4094e-14 | 5.4094e-14 | -0.72548 | -0.72548 | -0.39144 | -0.39144 | 0.6272 | 0.6272 | 0.6272 | 1.5863 | 1.5863 | 1.5863 | 1.5863 | 1.5863 | -1.129 | -1.129 | -0.47715 | -0.59479 | 1.2102 | 1.6921 | 1.6921 | 4.8539 | 4.8539 | 4.8539 | 5.0264 | 5.4769 | 4.9041 | 4.9041 | 4.9041 | 4.9041 | 4.9041 | 4.9041 | 4.9041 | 4.9041 | 0 | 5.4094e-14 | 5.4094e-14 | -0.72548 | -0.39144 | 0.6272 | 1.5863 | -1.129 | -0.47715 | -0.59479 | 1.2102 | 1.6921 | 4.8539 | 5.0264 | 5.4769 | 4.9041
|  |  | 0 | LOBI3B_LOBIT2_1 | LOBI3B_LOBIT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5885 | 2.5885 | 2.5885 | 0.64704 | 0.64044 | 2.127 | 2.127 | 2.127 | 2.127 | 2.127 | 2.127 | 2.127 | 2.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5885 | 0.64704 | 0.64044 | 2.127
|  |  | 0 |  | lne_AL048A_GRNA1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | CHAP1-_AL048A_1 | lne_CHAP1-_AL048A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  | lne_AL048B_GRNA1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.3686 | -0.3686 | -0.3686 | -1.3036 | -1.3036 | -1.3036 | -1.3036 | -1.3036 | -0.80089 | -0.80089 | -0.79458 | -0.82307 | -0.81973 | -1.272 | -1.272 | -0.805 | -0.805 | -0.805 | -1.2607 | -0.82438 | -1.2677 | -1.2677 | -1.2677 | -1.2677 | -1.2677 | -1.2677 | -1.2677 | -1.2677 | 0 | 0 | 0 | 0 | 0 | -0.3686 | -1.3036 | -0.80089 | -0.79458 | -0.82307 | -0.81973 | -1.272 | -0.805 | -1.2607 | -0.82438 | -1.2677
|  |  | 0 |  | lne_CHAP1-_AL048B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0137 | -1.0137 | -1.0137 | -1.9563 | -1.9563 | -1.9563 | -1.9563 | -1.9563 | -1.1982 | -1.1982 | -1.1888 | -1.2314 | -1.2264 | -1.9008 | -1.9008 | -1.2044 | -1.2044 | -1.2044 | -1.884 | -1.2333 | -1.8945 | -1.8945 | -1.8945 | -1.8945 | -1.8945 | -1.8945 | -1.8945 | -1.8945 | 0 | 0 | 0 | 0 | 0 | -1.0137 | -1.9563 | -1.1982 | -1.1888 | -1.2314 | -1.2264 | -1.9008 | -1.2044 | -1.884 | -1.2333 | -1.8945
|  |  | 0 |  | CHAP08_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.6063e-05 | -6.6063e-05 | -6.6063e-05 | -6.6932e-05 | -6.6932e-05 | -6.6932e-05 | -6.6932e-05 | -6.6932e-05 | -4.0743e-05 | -4.0743e-05 | -4.0422e-05 | -4.1871e-05 | -4.1702e-05 | -6.4486e-05 | -6.4486e-05 | -4.0952e-05 | -4.0952e-05 | -4.0952e-05 | -6.3917e-05 | -4.1938e-05 | -6.4272e-05 | -6.4272e-05 | -6.4272e-05 | -6.4272e-05 | -6.4272e-05 | -6.4272e-05 | -6.4272e-05 | -6.4272e-05 | 0 | 0 | 0 | 0 | 0 | -6.6063e-05 | -6.6932e-05 | -4.0743e-05 | -4.0422e-05 | -4.1871e-05 | -4.1702e-05 | -6.4486e-05 | -4.0952e-05 | -6.3917e-05 | -4.1938e-05 | -6.4272e-05
|  |  | 0 | CHAP3-_SOLWAY | CHAP3-_SOLWAY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2312e-27 | 3.2312e-27 | 3.2312e-27 | 1.4619e-22 | 1.4619e-22 | 1.4619e-22 | 1.4619e-22 | 1.4619e-22 | -1.8168e-18 | -1.8168e-18 | 5.9067e-19 | -1.5795e-18 | -4.8668e-18 | 1.1058e-19 | 1.1058e-19 | 1.0078e-18 | 1.0078e-18 | 1.0078e-18 | -1.3653e-21 | 2.5534e-18 | -2.2374e-19 | -2.2374e-19 | -2.2374e-19 | -2.2374e-19 | -2.2374e-19 | -2.2374e-19 | -2.2374e-19 | -2.2374e-19 | 0 | 0 | 0 | 0 | 0 | 3.2312e-27 | 1.4619e-22 | -1.8168e-18 | 5.9067e-19 | -1.5795e-18 | -4.8668e-18 | 1.1058e-19 | 1.0078e-18 | -1.3653e-21 | 2.5534e-18 | -2.2374e-19
|  |  | 0 | CHAP3A1 | CHAP3A1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | CHAP3A2 | CHAP3A2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | CHAP1-_CHAP3-_1 | CHAP1-_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | CHAP1-_CHAP3-_2 | CHAP1-_CHAP3-_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | CHAP1-_M1-_1 | CHAP1-_M1-_1 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP1-_M1-_2 | CHAP1-_M1-_2 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP1-_R1-_1 | CHAP1-_R1-_1 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | HARK | HARK | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | DUMF-2 | DUMF-2 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | ECCF-2 | ECCF-2 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA-2 | GRNA-2 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | DUMF-1 | DUMF-1 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | ECCF-1 | ECCF-1 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP1-_T1 | CHAP1-_T1 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP1-_T2 | CHAP1-_T2 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA-1 | GRNA-1 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STCR3- | STCR3- | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STCR3-_STCR0G | STCR3-_STCR0G | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STCR0G-_2 | STCR0G-_2 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STCR0G-_1 | STCR0G-_1 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STRC0G-_STCRLVT | STRC0G-_STCRLVT | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STCR_AUX | STCR_AUX | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STCR_DIESEL | STCR_DIESEL | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | MINS3- | MINS3- | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | MINS3-_MINSC | MINS3-_MINSC | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | MINS0G | MINS0G | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | EWEH3- | EWEH3- | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | EWEH3-_EWEH0G_1 | EWHC3-_EWHC0G_1 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | EWEH0G | EWEH0G | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA1-_SGT1 | GRNA1-_SGT1 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA1-_SGT2 | GRNA1-_SGT2 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA1-_EWEH | GRNA1-_EWEH | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA4-_M1-_SGT1 | GRNA4-_M1-_SGT1 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP1-_GRNA1 | CHAP1-_GRNA1 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | EWEH3 | EWEH3 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | EWEH3-_GRID1A-_WG2 | EWEH3-_GRID1A-_WG2 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | EWEH0G_2 | EWEH0G_2 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | HARK4 | HARK4 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA4-_M1 | GRNA4-_M1 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | CHAP2-_GRNA1 | CHAP2-_GRNA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | HAWI | CHAP2-_GRNA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lines are on SLD
Not used in simulation
Vlookup
Note on E9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 132kV line to Harker
Note on E15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: section of line from Chapelcross to T-off to Dumfries sector 414
Note on E21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Langholm 33kV A to Langholm T1
Note on E22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Langholm 33kV B to Langholm T2
Note on E29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Section of line between Chapelcross and Lockerbie going to Dumfries Sector 414
Note on E39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable section of 132kV line A from Chapelcross 132kV to Getna
Note on E40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable section of 132kV line A from Chapelcross 132kV to Getna
Note on E41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable section of 132kV line B from Chapelcross 132kV to Getna
Note on E42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Overhead line B from Chapelcross 132kV to Getna
Note on E43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Gretna 33kV to T junction of line from Chapelcross to Langholm

## Lines - Active Power
Lines - Active Power
Results
Lines
|  |  |  | Name in Simulation SLD |  | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[6 empty] | Active Power >>> | [36 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  | network | Name |  | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  | 0 |  | lne_CHAP1-_HAKB1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  | CRAG5B_LAHO5-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7212e-08 | 2.118e-08 | 2.2107e-08 | 2.2107e-08 | 2.1958e-08 | 2.1958e-08 | 2.1958e-08 | 2.2058e-08 | 2.1967e-08 | 2.1947e-08 | 2.1947e-08 | 2.1947e-08 | 2.1947e-08 | 2.1947e-08 | 2.1947e-08 | 2.1947e-08 | 2.1947e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7212e-08 | 2.118e-08 | 2.2107e-08 | 2.1958e-08 | 2.2058e-08 | 2.1967e-08 | 2.1947e-08
|  |  | 0 | CHAPX3_LAHO3B_1 | CHAPX3_LAHO3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.203 | 2.203 | 1.0958 | 1.0958 | 1.0958 | 1.0957 | 1.0957 | 3.519 | 3.519 | 3.519 | 3.519 | 3.519 | 3.519 | 3.519 | 3.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.203 | 1.0958 | 1.0957 | 1.0957 | 3.519
|  |  | 0 | LOBI3B_MOFTT2_1 | LOBI3B_MOFTT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5842 | 2.4534 | 2.4534 | 2.4534 | 2.4534 | 2.4534 | 2.4534 | 2.4534 | 2.4534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5842 | 2.4534
|  |  | 0 |  | lne_CHAP1-_DUMF1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | CHAP3-_LOBI3B_1 | CHAP3-_LOBI3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6102 | 15.6102 | 15.6102 | 7.5441 | 12.4343 | 10.2782 | 10.2782 | 10.2782 | 10.2782 | 10.2782 | 10.2782 | 10.2782 | 10.2782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6102 | 7.5441 | 12.4343 | 10.2782
|  |  | 0 |  | CHAP3-_CHAPX1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5853 | 15.5853 | 15.5853 | 15.634 | 13.4472 | 10.9826 | 10.9826 | 10.9826 | 10.9826 | 10.9826 | 10.9826 | 10.9826 | 10.9826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5853 | 15.634 | 13.4472 | 10.9826
|  |  | 0 | CHAPX4_KIBAT1_1 | CHAPX4_KIBAT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7693 | 2.0676 | 1.3723 | 1.3723 | 1.3723 | 1.3723 | 1.3723 | 1.3723 | 1.3723 | 1.3723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7693 | 2.0676 | 1.3723
|  |  | 0 | CHAPX4_MOFTT1_1 | CHAPX4_MOFTT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4053 | 3.2764 | 1.9365 | 1.9365 | 1.9365 | 1.9365 | 1.9365 | 1.9365 | 1.9365 | 1.9365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4053 | 3.2764 | 1.9365
|  |  | 0 | CHAP3-_CHAPX3_1 | CHAP3-_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2105 | -2.2105 | -1.1031 | -1.1031 | -1.1031 | -1.1032 | -1.1032 | -5.8634 | -5.8634 | -5.8634 | -5.8634 | -5.8634 | -5.8634 | -5.8634 | -5.8634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2105 | -1.1031 | -1.1032 | -1.1032 | -5.8634
|  |  | 0 | GRNA3A_GRNAT1_1 | GRNA3A_GRNAT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0074753 | 0.0074753 | 0.0072647 | 0.0072647 | 0.0072647 | 0.0074765 | 0.0074412 | 2.331 | 2.331 | 2.331 | 2.331 | 2.331 | 2.331 | 2.331 | 2.331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0074753 | 0.0072647 | 0.0074765 | 0.0074412 | 2.331
|  |  | 0 | LOBI3A_LOBIT1_1 | LOBI3A_LOBIT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.7603 | 14.7603 | 14.7603 | 7.3537 | 7.3534 | 7.2346 | 7.2346 | 7.2346 | 7.2346 | 7.2346 | 7.2346 | 7.2346 | 7.2346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.7603 | 7.3537 | 7.3534 | 7.2346
|  |  | 0 |  | LAHO3A_LAHOT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.7881 | 9.5608 | 6.3641 | 6.3641 | 6.3642 | 6.3642 | 6.3642 | 6.3642 | 6.3642 | 3.9467 | 3.9467 | 3.9467 | 3.9467 | 3.9467 | 3.9467 | 3.9467 | 3.9467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.7881 | 9.5608 | 6.3641 | 6.3642 | 6.3642 | 6.3642 | 3.9467
|  |  | 0 |  | LAHO3B_LAHOT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2081e-08 | 2.2081e-08 | 2.1817e-08 | 2.1817e-08 | 2.1817e-08 | 2.2166e-08 | 2.2061e-08 | 2.4074 | 2.4074 | 2.4074 | 2.4074 | 2.4074 | 2.4074 | 2.4074 | 2.4074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2081e-08 | 2.1817e-08 | 2.2166e-08 | 2.2061e-08 | 2.4074
|  |  | 0 | MIBI3-_MIBIT1_1 | MIBI3-_MIBIT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4908 | 7.8586 | 5.2319 | 5.2317 | 5.2317 | 5.2318 | 5.2318 | 5.2318 | 5.2318 | 5.2318 | 5.2317 | 5.2317 | 5.2317 | 5.2317 | 5.2317 | 5.2317 | 5.2317 | 5.2317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4908 | 7.8586 | 5.2319 | 5.2317 | 5.2318 | 5.2318 | 5.2318 | 5.2317
|  |  | 0 | GRNA3B_GRNAT2_1 | GRNA3B_GRNAT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.395 | 10.7762 | 10.7762 | 7.1726 | 7.1726 | 7.1726 | 7.1725 | 7.1726 | 4.8362 | 4.8362 | 4.8362 | 4.8362 | 4.8362 | 4.8362 | 4.8362 | 4.8362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.395 | 10.7762 | 7.1726 | 7.1725 | 7.1726 | 4.8362
|  |  | 0 | MIBI3-_LAHO3A_1 | MIBI3-_LAHO3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.0469 | 10.5959 | 6.7601 | 6.7601 | 6.7629 | 6.7629 | 6.7629 | 6.7508 | 6.7524 | 4.0957 | 4.0957 | 4.0957 | 4.0957 | 4.0957 | 4.0957 | 4.0957 | 4.0957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.0469 | 10.5959 | 6.7601 | 6.7629 | 6.7508 | 6.7524 | 4.0957
|  |  | 0 | LAHO3B_NEWCT1_1 | LAHO3B_NEWCT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1963 | 2.1963 | 1.0941 | 1.0941 | 1.0941 | 1.094 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1963 | 1.0941 | 1.094 | 1.0941 | 1.0941
|  |  | 0 | CHAP3-_MIBI3-_1 | CHAP3-_MIBI3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50104 | 0.50104 | 0.50103 | 0.50103 | 0.50103 | 0.50103 | 0.50103 | 0.50103 | 0.50103 | 0.50103 | 0.50107 | 0.50107 | 11.1676 | 24.256 | 16.7204 | 12.7106 | 12.7106 | 7.6421 | 7.6421 | 7.6421 | 7.6171 | 7.6244 | 4.9044 | 4.9044 | 4.9044 | 4.9044 | 4.9044 | 4.9044 | 4.9044 | 4.9044 | 0 | 0 | 0 | 0 | 0.50104 | 0.50103 | 0.50103 | 0.50107 | 11.1676 | 24.256 | 16.7204 | 12.7106 | 7.6421 | 7.6171 | 7.6244 | 4.9044
|  |  | 0 | ANANT1_CHAP3-_1 | ANANT1_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2382 | 12.2382 | 9.1505 | 6.0823 | 6.0825 | 6.0818 | 6.0818 | 6.0827 | 6.0827 | 6.0827 | 6.0821 | 6.0823 | 6.1115 | 6.1115 | 6.1115 | 6.1115 | 6.1115 | 6.1115 | 6.1115 | 6.1115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2382 | 9.1505 | 6.0823 | 6.0825 | 6.0818 | 6.0827 | 6.0821 | 6.0823 | 6.1115
|  |  | 0 |  | CARU3A_CHAPX1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0623e-08 | -1.0623e-08 | -1.0623e-08 | -1.0945e-08 | -1.0907e-08 | -1.1042e-08 | -1.1042e-08 | -1.1042e-08 | -1.1042e-08 | -1.1042e-08 | -1.1042e-08 | -1.1042e-08 | -1.1042e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0623e-08 | -1.0945e-08 | -1.0907e-08 | -1.1042e-08
|  |  | 0 | ANANT2_CHAP3-_1 | ANANT2_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2387 | 12.2387 | 9.1508 | 6.0824 | 6.0825 | 6.0819 | 6.0819 | 6.0828 | 6.0828 | 6.0828 | 6.0822 | 6.0824 | 6.0524 | 6.0524 | 6.0524 | 6.0524 | 6.0524 | 6.0524 | 6.0524 | 6.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2387 | 9.1508 | 6.0824 | 6.0825 | 6.0819 | 6.0828 | 6.0822 | 6.0824 | 6.0524
|  |  | 0 | EWEH3-_MIBI3-_1 | EWHC3-_MIBI3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50056 | 0.50056 | 0.50056 | 0.50056 | 0.50056 | 0.50055 | 0.50055 | 0.50055 | 0.50055 | 0.50055 | 0.50062 | 0.50062 | 0.50066 | 0.50069 | 0.50065 | 0.50062 | 0.50062 | -4.4466 | -4.4466 | -4.4466 | -4.453 | -4.45 | -4.4597 | -4.4597 | -4.4597 | -4.4597 | -4.4597 | -4.4597 | -4.4597 | -4.4597 | 0 | 0 | 0 | 0 | 0.50056 | 0.50056 | 0.50055 | 0.50062 | 0.50066 | 0.50069 | 0.50065 | 0.50062 | -4.4466 | -4.453 | -4.45 | -4.4597
|  |  | 0 |  | CRAG5A_LAHO5-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7411e-08 | -2.1377e-08 | -2.2306e-08 | -2.2306e-08 | -2.2156e-08 | -2.2156e-08 | -2.2156e-08 | -2.226e-08 | -2.2168e-08 | -2.2145e-08 | -2.2145e-08 | -2.2145e-08 | -2.2145e-08 | -2.2145e-08 | -2.2145e-08 | -2.2145e-08 | -2.2145e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7411e-08 | -2.1377e-08 | -2.2306e-08 | -2.2156e-08 | -2.226e-08 | -2.2168e-08 | -2.2145e-08
|  |  | 0 | CHAPX4_LOBI3A_1 | CHAPX4_LOBI3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.1747 | -5.3439 | -3.3088 | -3.3088 | -3.3088 | -3.3088 | -3.3088 | -3.3088 | -3.3088 | -3.3088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.1747 | -5.3439 | -3.3088
|  |  | 0 | CHAPX1_LOBI3A_1 | CHAPX1_LOBI3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5345 | 15.5345 | 15.5345 | 15.5861 | 13.4118 | 10.9593 | 10.9593 | 10.9593 | 10.9593 | 10.9593 | 10.9593 | 10.9593 | 10.9593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5345 | 15.5861 | 13.4118 | 10.9593
|  |  | 0 | CHAP3-_GRNA3B_1 | CHAP3-_GRNA3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9233 | 11.0566 | 11.0566 | 7.2985 | 7.2985 | 7.2985 | 7.2948 | 7.2955 | 4.8909 | 4.8909 | 4.8909 | 4.8909 | 4.8909 | 4.8909 | 4.8909 | 4.8909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9233 | 11.0566 | 7.2985 | 7.2948 | 7.2955 | 4.8909
|  |  | 0 | CHAP3-_MINS3-_1 | CHAP3-_MINS3-_1 | 0 | 0 | 0 | 0 | 0 | 0.5024 | 0.5024 | 0.50239 | 0.50239 | 0.50236 | 0.50236 | 0.50236 | 0.50232 | 0.50232 | 0.50232 | 0.50232 | 0.50232 | 0.5027 | 0.5027 | 0.50274 | -19.2368 | -19.2326 | -19.2465 | -19.2465 | -19.2055 | -19.2055 | -19.2055 | -19.242 | -19.2383 | -19.2452 | -19.2452 | -19.2452 | -19.2452 | -19.2452 | -19.2452 | -19.2452 | -19.2452 | 0 | 0 | 0 | 0.5024 | 0.50239 | 0.50236 | 0.50232 | 0.5027 | 0.50274 | -19.2368 | -19.2326 | -19.2465 | -19.2055 | -19.242 | -19.2383 | -19.2452
|  |  | 0 | CHAP3-_STCR3-_1 | CHAP3-_STCR3-_1 | 0 | 0 | -1.1415e-08 | -1.1415e-08 | -1.1415e-08 | -0.5024 | -0.5024 | -1.0034 | -1.0034 | -1.032 | -1.032 | -1.032 | -1.122 | -1.122 | -1.122 | -1.122 | -1.122 | -25.5556 | -25.5556 | -30.046 | -17.2609 | -24.6528 | -19.0103 | -19.0103 | -40.2792 | -40.2792 | -40.2792 | -32.2178 | -34.9124 | -30.0579 | -30.0579 | -30.0579 | -30.0579 | -30.0579 | -30.0579 | -30.0579 | -30.0579 | 0 | -1.1415e-08 | -1.1415e-08 | -0.5024 | -1.0034 | -1.032 | -1.122 | -25.5556 | -30.046 | -17.2609 | -24.6528 | -19.0103 | -40.2792 | -32.2178 | -34.9124 | -30.0579
|  |  | 0 | LOBI3B_LOBIT2_1 | LOBI3B_LOBIT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.7916 | 14.7916 | 14.7916 | 7.367 | 7.3668 | 7.4888 | 7.4888 | 7.4888 | 7.4888 | 7.4888 | 7.4888 | 7.4888 | 7.4888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.7916 | 7.367 | 7.3668 | 7.4888
|  |  | 0 |  | lne_AL048A_GRNA1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | CHAP1-_AL048A_1 | lne_CHAP1-_AL048A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  | lne_AL048B_GRNA1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2666e-08 | 4.2666e-08 | 4.2666e-08 | 0.089274 | 0.089274 | 0.089274 | 0.089274 | 0.089274 | 0.048097 | 0.048097 | 0.047718 | 0.049429 | 0.049229 | 0.070616 | 0.070616 | 0.048344 | 0.048344 | 0.048344 | 0.070013 | 0.049508 | 0.070398 | 0.070398 | 0.070398 | 0.070398 | 0.070398 | 0.070398 | 0.070398 | 0.070398 | 0 | 0 | 0 | 0 | 0 | 4.2666e-08 | 0.089274 | 0.048097 | 0.047718 | 0.049429 | 0.049229 | 0.070616 | 0.048344 | 0.070013 | 0.049508 | 0.070398
|  |  | 0 |  | lne_CHAP1-_AL048B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9126e-05 | 5.9126e-05 | 5.9126e-05 | 0.089581 | 0.089581 | 0.089581 | 0.089581 | 0.089581 | 0.048286 | 0.048286 | 0.047906 | 0.049624 | 0.049423 | 0.070918 | 0.070918 | 0.048535 | 0.048535 | 0.048535 | 0.070312 | 0.049703 | 0.070699 | 0.070699 | 0.070699 | 0.070699 | 0.070699 | 0.070699 | 0.070699 | 0.070699 | 0 | 0 | 0 | 0 | 0 | 5.9126e-05 | 0.089581 | 0.048286 | 0.047906 | 0.049624 | 0.049423 | 0.070918 | 0.048535 | 0.070312 | 0.049703 | 0.070699
|  |  | 0 |  | CHAP08_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4699e-12 | 6.4699e-12 | 6.4699e-12 | 6.556e-12 | 6.556e-12 | 6.556e-12 | 6.556e-12 | 6.556e-12 | 4.0008e-12 | 4.0008e-12 | 3.9671e-12 | 4.1085e-12 | 4.0925e-12 | 6.3278e-12 | 6.3278e-12 | 4.0187e-12 | 4.0187e-12 | 4.0187e-12 | 6.2697e-12 | 4.1164e-12 | 6.2973e-12 | 6.2973e-12 | 6.2973e-12 | 6.2973e-12 | 6.2973e-12 | 6.2973e-12 | 6.2973e-12 | 6.2973e-12 | 0 | 0 | 0 | 0 | 0 | 6.4699e-12 | 6.556e-12 | 4.0008e-12 | 3.9671e-12 | 4.1085e-12 | 4.0925e-12 | 6.3278e-12 | 4.0187e-12 | 6.2697e-12 | 4.1164e-12 | 6.2973e-12
|  |  | 0 | CHAP3-_SOLWAY | CHAP3-_SOLWAY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3269e-12 | -2.3269e-12 | -2.3269e-12 | -2.355e-12 | -2.355e-12 | -2.355e-12 | -2.355e-12 | -2.355e-12 | -1.4335e-12 | -1.4335e-12 | -1.4222e-12 | -1.4732e-12 | -1.4673e-12 | -2.2689e-12 | -2.2689e-12 | -1.4409e-12 | -1.4409e-12 | -1.4409e-12 | -2.2489e-12 | -1.4756e-12 | -2.2614e-12 | -2.2614e-12 | -2.2614e-12 | -2.2614e-12 | -2.2614e-12 | -2.2614e-12 | -2.2614e-12 | -2.2614e-12 | 0 | 0 | 0 | 0 | 0 | -2.3269e-12 | -2.355e-12 | -1.4335e-12 | -1.4222e-12 | -1.4732e-12 | -1.4673e-12 | -2.2689e-12 | -1.4409e-12 | -2.2489e-12 | -1.4756e-12 | -2.2614e-12
|  |  | 0 | CHAP3A1 | CHAP3A1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | CHAP3A2 | CHAP3A2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | CHAP1-_CHAP3-_1 | CHAP1-_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | CHAP1-_CHAP3-_2 | CHAP1-_CHAP3-_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | CHAP1-_M1-_1 | CHAP1-_M1-_1 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP1-_M1-_2 | CHAP1-_M1-_2 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP1-_R1-_1 | CHAP1-_R1-_1 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | HARK | HARK | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | DUMF-2 | DUMF-2 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | ECCF-2 | ECCF-2 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA-2 | GRNA-2 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | DUMF-1 | DUMF-1 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | ECCF-1 | ECCF-1 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP1-_T1 | CHAP1-_T1 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP1-_T2 | CHAP1-_T2 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA-1 | GRNA-1 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STCR3- | STCR3- | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STCR3-_STCR0G | STCR3-_STCR0G | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STCR0G-_2 | STCR0G-_2 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STCR0G-_1 | STCR0G-_1 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STRC0G-_STCRLVT | STRC0G-_STCRLVT | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STCR_AUX | STCR_AUX | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | STCR_DIESEL | STCR_DIESEL | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | MINS3- | MINS3- | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | MINS3-_MINSC | MINS3-_MINSC | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | MINS0G | MINS0G | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | EWEH3- | EWEH3- | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | EWEH3-_EWEH0G_1 | EWHC3-_EWHC0G_1 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | EWEH0G | EWEH0G | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA1-_SGT1 | GRNA1-_SGT1 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA1-_SGT2 | GRNA1-_SGT2 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA1-_EWEH | GRNA1-_EWEH | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA4-_M1-_SGT1 | GRNA4-_M1-_SGT1 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP1-_GRNA1 | CHAP1-_GRNA1 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | EWEH3 | EWEH3 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | EWEH3-_GRID1A-_WG2 | EWEH3-_GRID1A-_WG2 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | EWEH0G_2 | EWEH0G_2 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | HARK4 | HARK4 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | GRNA4-_M1 | GRNA4-_M1 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | 0 | CHAP2-_GRNA1 | CHAP2-_GRNA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | HAWI | CHAP2-_GRNA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lines are on SLD
Not used in simulation
Vlookup
Note on E9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 132kV line to Harker
Note on E15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: section of line from Chapelcross to T-off to Dumfries sector 414
Note on E21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Langholm 33kV A to Langholm T1
Note on E22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Langholm 33kV B to Langholm T2
Note on E29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Section of line between Chapelcross and Lockerbie going to Dumfries Sector 414
Note on E39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable section of 132kV line A from Chapelcross 132kV to Getna
Note on E40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable section of 132kV line A from Chapelcross 132kV to Getna
Note on E41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable section of 132kV line B from Chapelcross 132kV to Getna
Note on E42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Overhead line B from Chapelcross 132kV to Getna
Note on E43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Gretna 33kV to T junction of line from Chapelcross to Langholm