## Generators - Active Power
Generators - Active Power
Results
Lines
[6 empty] | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
Active Power >>>
|  |  | Name | Min P | Max P | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  | STCR5-_1 | 0 | 45 | 0 | 0 | 0 | 4.5064 | 4.5435 | 4.5435 | 5.0326 | 5.0326 | 5.5335 | 5.562 | 5.5675 | 5.5721 | 5.5721 | 5.6333 | 5.6942 | 5.6942 | 5.6578 | 18.0959 | 30.8232 | 35.5836 | 6.0023 | 21.5371 | 32.4801 | 26.6612 | 22.2233 | 33.9945 | 23.8355 | 35.3384 | 35.3912 | 34.0537 | 29.1969 | 29.2111 | 29.2105 | 28.9439 | 28.9748 | 28.9748 | 37.2001 | 4.5 | 4.512 | 4.512 | 5.0106 | 5.514 | 5.5491 | 5.6469 | 26.1569 | 30.8845 | 17.5336 | 25.2146 | 19.3506 | 41.8135 | 33.1976 | 36.0638 | 30.9127
|  |  | CRAG0A_1 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | CRAG0B_1 | 0 | 2.2 | 2e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10
|  |  | EWHC0G_1 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7347e-18 | 0 | 0 | 4.3368e-19 | 4.3368e-19 | 0 | 7.0644e-07 | 7.0644e-07 | 4.3368e-19 | 0 | 0 | 1.1102e-16 | 2.4 | 2.4 | 2.4 | 2.4 | 3 | 3 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 5
|  |  | WYSB0G_1 | 0 | 10 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
|  |  | MINS0G_1 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.9389e-18 | 0 | 0 | 0 | 0 | 0 | -1.7347e-18 | 8.1462e-07 | 8.1462e-07 | 0 | -2.7756e-17 | 1.1102e-16 | 0 | 7.36 | 7.36 | 7.36 | 7.36 | 9.2 | 9.2 | 16.56 | 16.56 | 16.56 | 16.56 | 16.56 | 16.56 | 16.56 | 16.56 | 16.56 | 16.56 | 16.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  |  | WTG_EWEH0G_1 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3878e-17 | 1.3878e-17 | -1.3878e-17 | 7.36 | 7.36 | 7.36 | 7.36 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
End Of Sheet
Vlookup
Copy and paste from PF
|  |  | STCR5-_1 | 0 | 45 | 0 | 0 | 0 | 4.5064 | 4.5435 | 4.5435 | 5.0326 | 5.0326 | 5.5335 | 5.562 | 5.5675 | 5.5721 | 5.5721 | 5.6333 | 5.6942 | 5.6942 | 5.6578 | 18.0959 | 30.8232 | 35.5836 | 6.0023 | 21.5371 | 32.4801 | 26.6612 | 22.2233 | 33.9945 | 23.8355 | 35.3384 | 35.3912 | 34.0537 | 29.1969 | 29.2111 | 29.2105 | 28.9439 | 28.9748 | 28.9748 | 37.2001
|  |  | WTG_EWEH0G_1 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3878e-17 | 1.3878e-17 | -1.3878e-17 | 7.36 | 7.36 | 7.36 | 7.36 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2
|  |  | EWHC0G_1 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7347e-18 | 0 | 0 | 4.3368e-19 | 4.3368e-19 | 0 | 7.0644e-07 | 7.0644e-07 | 4.3368e-19 | 0 | 0 | 1.1102e-16 | 2.4 | 2.4 | 2.4 | 2.4 | 3 | 3 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
|  |  | CRAG0B_1 | 0 | 2.2 | 2e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10 | 2e-10
|  |  | CRAG0A_1 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MINS0G_1 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.9389e-18 | 0 | 0 | 0 | 0 | 0 | -1.7347e-18 | 8.1462e-07 | 8.1462e-07 | 0 | -2.7756e-17 | 1.1102e-16 | 0 | 7.36 | 7.36 | 7.36 | 7.36 | 9.2 | 9.2 | 16.56 | 16.56 | 16.56 | 16.56 | 16.56 | 16.56 | 16.56 | 16.56 | 16.56 | 16.56 | 16.56

## Generators - Reactive Power
Generators - Reactive Power
Results
Lines
[6 empty] | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[6 empty] | Reactive Power >>> | [36 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  | Name | Min Q | Max Q | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  | STCR5-_1 | -18.6347 | 18.6347 | 0 | 0 | 0 | 0.97779 | -7.2991 | -7.2991 | -6.0756 | -6.0756 | -5.9826 | -5.9797 | -6.5254 | -6.8646 | -6.8646 | -6.8512 | -7.4936 | -7.4936 | -6.4698 | -7.3485 | -7.3804 | -7.9392 | -5.8948 | -6.4243 | -6.406 | -7.0876 | -6.754 | -6.0383 | -5.3013 | -4.6032 | -5.124 | -5.5124 | -5.8748 | -5.8598 | -5.8599 | -5.8288 | -5.9079 | -5.9079 | -6.1173 | 0.914 | -4.2712 | -4.2712 | -3.5395 | -3.8689 | -4.8861 | -5.8352 | -1.0101 | -0.50482 | -3.203 | -3.616 | -5.2192 | -2.5609 | -5.4741 | -5.0904 | -5.9665
|  |  | CRAG0A_1 | -3.4697 | 3.4697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | CRAG0B_1 | -0.78137 | 0.78137 | 1.2925e-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2925e-26 | 0 | -6.4623e-27 | 6.4623e-27 | -6.4623e-27 | -6.4623e-27 | 0 | -6.4623e-27 | 0 | 0 | 0 | -6.4623e-27 | -6.4623e-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2925e-26 | -1.2925e-26 | 6.4623e-27 | -1.2925e-26 | 6.4623e-27 | 0 | 0
|  |  | EWHC0G_1 | -3.944 | 3.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37244 | 0.3767 | 0.09158 | -0.085454 | -0.085454 | -0.072619 | -0.4029 | -0.4029 | 0.12936 | 0.68791 | 1.3597 | 3.0799 | 0.41848 | 3.944 | 3.944 | 2.76 | 2.4784 | 3.4124 | 2.5156 | 3.3903 | 3.112 | 2.8611 | 2.4787 | 2.4874 | 2.4873 | 1.987 | 2.0254 | 2.0254 | 2.2043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.944 | 3.4283 | 3.7246 | 2.6496
|  |  | WYSB0G_1 | 0 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MINS0G_1 | -10.49 | 14.13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5144 | 1.5144 | 1.7959 | 1.8082 | 0.98211 | 0.46909 | 0.46909 | 0.50628 | -0.45097 | -0.45097 | 1.0916 | 2.7098 | 4.6556 | 4.2704 | 0.33248 | 3.0286 | 4.5901 | 2.8293 | 2.2357 | 4.8928 | 3.1739 | 5.657 | 4.8674 | 4.1549 | 3.0691 | 3.0938 | 3.0935 | 3.1072 | 2.9908 | 2.9908 | 3.4962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8305 | 6.5513 | 3.1258 | 9.7571 | 4.7087 | 5.5466 | 3.7187
|  |  | WTG_EWEH0G_1 | -10.92 | 15.6422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1286 | -1.4082 | -0.5424 | -0.71379 | -2.0208 | -0.81733 | -0.12056 | -0.90627 | -1.0178 | 0.16905 | 0.09103 | 1.1967 | 0.84252 | 0.52293 | 0.044045 | 0.055088 | 0.054976 | 0.061131 | 0.0089023 | 0.0089023 | -0.69168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
End Of Sheet
Vlookup
Copy and paste from PF
|  |  | STCR5-_1 | -18.6347 | 18.6347 | 0 | 0 | 0 | 0.97779 | -7.2991 | -7.2991 | -6.0756 | -6.0756 | -5.9826 | -5.9797 | -6.5254 | -6.8646 | -6.8646 | -6.8512 | -7.4936 | -7.4936 | -6.4698 | -7.3485 | -7.3804 | -7.9392 | -5.8948 | -6.4243 | -6.406 | -7.0876 | -6.754 | -6.0383 | -5.3013 | -4.6032 | -5.124 | -5.5124 | -5.8748 | -5.8598 | -5.8599 | -5.8288 | -5.9079 | -5.9079 | -6.1173
|  |  | WTG_EWEH0G_1 | -10.92 | 15.6422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1286 | -1.4082 | -0.5424 | -0.71379 | -2.0208 | -0.81733 | -0.12056 | -0.90627 | -1.0178 | 0.16905 | 0.09103 | 1.1967 | 0.84252 | 0.52293 | 0.044045 | 0.055088 | 0.054976 | 0.061131 | 0.0089023 | 0.0089023 | -0.69168
|  |  | EWHC0G_1 | -3.944 | 3.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37244 | 0.3767 | 0.09158 | -0.085454 | -0.085454 | -0.072619 | -0.4029 | -0.4029 | 0.12936 | 0.68791 | 1.3597 | 3.0799 | 0.41848 | 3.944 | 3.944 | 2.76 | 2.4784 | 3.4124 | 2.5156 | 3.3903 | 3.112 | 2.8611 | 2.4787 | 2.4874 | 2.4873 | 1.987 | 2.0254 | 2.0254 | 2.2043
|  |  | CRAG0B_1 | -0.78137 | 0.78137 | 1.2925e-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2925e-26 | 0 | -6.4623e-27 | 6.4623e-27 | -6.4623e-27 | -6.4623e-27 | 0 | -6.4623e-27 | 0 | 0 | 0 | -6.4623e-27 | -6.4623e-27 | 0 | 0 | 0
|  |  | CRAG0A_1 | -3.4697 | 3.4697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MINS0G_1 | -10.49 | 14.13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5144 | 1.5144 | 1.7959 | 1.8082 | 0.98211 | 0.46909 | 0.46909 | 0.50628 | -0.45097 | -0.45097 | 1.0916 | 2.7098 | 4.6556 | 4.2704 | 0.33248 | 3.0286 | 4.5901 | 2.8293 | 2.2357 | 4.8928 | 3.1739 | 5.657 | 4.8674 | 4.1549 | 3.0691 | 3.0938 | 3.0935 | 3.1072 | 2.9908 | 2.9908 | 3.4962

## Generators - Rating
Generators - Rating
Results
Lines
|  |  |  | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
|  |  |  | Rating (MW) >>> | [36 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  | Name | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  | STCR5-_1 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 0.914 | -4.2712 | -4.2712 | -3.5395 | -3.8689 | -4.8861 | -5.8352 | -1.0101 | -0.50482 | -3.203 | -3.616 | -5.2192 | -2.5609 | -5.4741 | -5.0904 | -5.9665
|  |  | CRAG0A_1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | CRAG0B_1 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2925e-26 | -1.2925e-26 | 6.4623e-27 | -1.2925e-26 | 6.4623e-27 | 0 | 0
|  |  | EWHC0G_1 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.944 | 3.4283 | 3.7246 | 2.6496
|  |  | WYSB0G_1 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MINS0G_1 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8305 | 6.5513 | 3.1258 | 9.7571 | 4.7087 | 5.5466 | 3.7187
|  |  | WTG_EWEH0G_1 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
End Of Sheet
Vlookup

## Busbars - Voltage(pu)
Busbars - Voltage(pu)
Results
Lines
[7 empty] | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[7 empty] | Magnitude (pu) >>> | V should be > 0 | [35 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  |  | Name | PF Name | Nom Volt (kV) | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  |  | ECCF1K | ECCF1K | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | CHAP1A- | CHAP1A- | 132 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | [5 empty] | 1.0061 | 1.0123 | 0.78984 | 0.78672 | 0.78672 | 0.79908 | 0.99367 | 0.79186 | 0.98928 | 0.80134 | 0.99203
|  |  |  | Terminal | Terminal | 33 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
|  |  |  | HAKB1- | HAKB1- | 132 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 1.0394 | 1.0394 | 1.0394 | 1.0394 | 1.0394 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151 | 1.1151
|  |  |  | Terminal(1) | Terminal(1) | 33 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Chapelcross 132kV BB |  |  | Y | CHAP1- | CHAP1- | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0108 | 1.0149 | 1.0149 | 1.0146 | 1.1444 | 1.1444 | 1.0099 | 1.0074 | 1.0043 | 1.0049 | 1.0072 | 1.0029 | 1.0005 | 1.0032 | 1.0031 | 0.99895 | 0.99923 | 0.99531 | 0.99656 | 0.99769 | 0.99939 | 0.99935 | 0.99935 | 0.99933 | 0.99952 | 0.99952 | 1.0022 | 0 | 0 | 0 | 0 | 0 | 1.0061 | 1.0123 | 0.78984 | 0.78672 | 0.78672 | 0.79908 | 0.99367 | 0.79186 | 0.98928 | 0.80134 | 0.99203
|  |  |  | ECCF1J | ECCF1J | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gretna 132kV |  |  | Y | GRNA1- | GRNA1- | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0151 | 1.0148 | 1.1449 | 1.1449 | 1.0098 | 1.0074 | 1.0046 | 1.0052 | 1.0078 | 1.004 | 1.0017 | 1.0042 | 1.0043 | 1.0005 | 1.0007 | 0.99714 | 0.99828 | 0.99932 | 1.0009 | 1.0008 | 1.0008 | 1.0008 | 1.001 | 1.001 | 1.0032 | 1.019 | 1.019 | 1.019 | 1.019 | 1.019 | 0 | 1.0128 | 0.79021 | 0.78709 | 0.78709 | 0.79945 | 0.99414 | 0.79224 | 0.98975 | 0.80172 | 0.9925
|  |  |  | DUMF1- | DUMF1- | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Langholm 33/11kV T1 |  |  |  | LAHOT1 | LAHOT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84036 | 0.89454 | 0.94361 | 0.94437 | 0.93863 | 0.9404 | 0.93491 | 0.93665 | 0.93823 | 0.94063 | 0.94058 | 0.94058 | 0.9676 | 0.96389 | 0.96389 | 0.96276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86427 | 0.92415 | 0.92114 | 0.9353 | 0.93343 | 0.96081
Middlebie 33kV BB |  |  |  | MIBI3- | MIBI3- | 33 | 0 | 0 | 0 | 0 | 1.0299 | 1.0299 | 1.0244 | 1.0244 | 1.0221 | 1.0221 | 1.0238 | 1.0248 | 1.0248 | 1.0247 | 1.0266 | 1.0266 | 1.0235 | 1.0203 | 1.0164 | 1.0065 | 1.0181 | 0.98728 | 0.99392 | 1.0045 | 1.0053 | 0.99984 | 1.0015 | 0.99639 | 0.99801 | 0.99947 | 1.0017 | 1.0016 | 1.0016 | 1.0046 | 1.0043 | 1.0043 | 1.0033 | 0 | 0 | 0 | 0 | 1.0162 | 1.0205 | 1.0244 | 0.98416 | 0.96473 | 0.96473 | 0.96755 | 0.98635 | 0.98357 | 0.99676 | 0.99503 | 1.0013
|  |  |  | CHAPX3 | CHAPX3 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0071 | 1.0076 | 1.0024 | 1.0029 | 0.99815 | 1.0004 | 1.0024 | 1.0054 | 1.0054 | 1.0054 | 0.99834 | 0.99365 | 0.99365 | 0.99224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99885 | 0.98468 | 0.99893 | 0.99657 | 0.9897
Lockerbie 33kV BB A |  |  |  | LOBI3A | LOBI3A | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94167 | 0.94221 | 0.95512 | 0.94661 | 0.95811 | 0.96931 | 0.9779 | 0.97695 | 0.9769 | 0.97725 | 0.97725 | 0.97574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92033 | 0.94507 | 0.952 | 0.97311
Moffat 33/11kV T2 |  |  |  | MOFTT2 | MOFTT2 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90082 | 0.94688 | 0.93779 | 0.93883 | 0.93878 | 0.93914 | 0.93914 | 0.93768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8942 | 0.93489
Langholm 33kV BB A |  |  |  | LAHO3A | LAHO3A | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84036 | 0.89454 | 0.94361 | 0.94437 | 0.93863 | 0.9404 | 0.93491 | 0.93665 | 0.93823 | 0.94063 | 0.94058 | 0.94058 | 0.9676 | 0.96389 | 0.96389 | 0.96276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86427 | 0.92415 | 0.92114 | 0.9353 | 0.93343 | 0.96081
Newcastleton 33/11kV T1 |  |  |  | NEWCT1 | NEWCT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99718 | 0.99771 | 0.9952 | 0.99569 | 0.99351 | 0.99575 | 0.99777 | 1.0008 | 1.0008 | 1.0008 | 0.99111 | 0.98691 | 0.98691 | 0.98551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98887 | 0.97997 | 0.9943 | 0.99192 | 0.98296
|  |  |  | CHAPX4 | CHAPX4 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90564 | 0.92921 | 0.9513 | 0.9601 | 0.95908 | 0.95903 | 0.95939 | 0.95939 | 0.95784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90401 | 0.92286 | 0.95516
Langholm 33/11kV T2 |  |  |  | LAHOT2 | LAHOT2 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0038 | 1.0043 | 1 | 1.0005 | 0.99665 | 0.99888 | 1.0009 | 1.004 | 1.0039 | 1.0039 | 0.99426 | 0.99007 | 0.99007 | 0.98867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99552 | 0.98315 | 0.99743 | 0.99506 | 0.98614
Annan 33/11kV T1 |  |  |  | ANANT1 | ANANT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.012 | 1.0066 | 1.0096 | 1.0175 | 1.01 | 1.0056 | 1.0106 | 1.0111 | 1.0037 | 1.0041 | 0.99716 | 0.99938 | 1.0014 | 1.0044 | 1.0044 | 1.0044 | 1.0043 | 1.0046 | 1.0046 | 1.0032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97736 | 0.97549 | 0.97549 | 0.99276 | 1.0024 | 0.98374 | 0.99794 | 0.99558 | 1.0007
Chapelcross 33kV BB |  |  |  | CHAP3- | CHAP3- | 33 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Gretna 33/11 kV T1 |  |  |  | GRNAT1 | GRNAT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0076 | 1.0081 | 1.003 | 1.0034 | 0.99867 | 1.0009 | 1.0029 | 1.006 | 1.0059 | 1.0059 | 0.99886 | 0.99021 | 0.99021 | 0.98879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99937 | 0.98519 | 0.99945 | 0.99709 | 0.98625
|  |  |  | CHAPX1 | CHAPX1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0024 | 1.0029 | 0.99725 | 0.9987 | 1.0013 | 1.0049 | 1.0054 | 1.0053 | 1.0053 | 1.0056 | 1.0056 | 1.0042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98249 | 0.99729 | 0.99556 | 1.0017
|  |  |  | WYSB3- | WYSB3- | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gretna 33kV BB A |  |  |  | GRNA3A | GRNA3A | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0076 | 1.0081 | 1.003 | 1.0034 | 0.99867 | 1.0009 | 1.0029 | 1.006 | 1.0059 | 1.0059 | 0.99886 | 0.99021 | 0.99021 | 0.98879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99937 | 0.98519 | 0.99945 | 0.99709 | 0.98625
Langholm 33kV BB B |  |  |  | LAHO3B | LAHO3B | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0038 | 1.0043 | 1 | 1.0005 | 0.99665 | 0.99888 | 1.0009 | 1.004 | 1.0039 | 1.0039 | 0.99426 | 0.99007 | 0.99007 | 0.98867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99552 | 0.98315 | 0.99743 | 0.99506 | 0.98614
|  |  |  | WYSB0G | WYSB0G | 0.69 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Lockerbie 33/11kV T2 |  |  |  | LOBIT2 | LOBIT2 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93405 | 0.95738 | 0.96033 | 0.9737 | 0.96491 | 0.96582 | 0.96578 | 0.96612 | 0.96612 | 0.96467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91944 | 0.97356 | 0.95422 | 0.96204
Lockerbie 33kV BB B |  |  |  | LOBI3B | LOBI3B | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93405 | 0.95738 | 0.96033 | 0.9737 | 0.96491 | 0.96583 | 0.96579 | 0.96613 | 0.96613 | 0.96467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91945 | 0.97357 | 0.95422 | 0.96205
Kirbank 33/11kV T1 |  |  |  | KIBAT1 | KIBAT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89451 | 0.9214 | 0.94652 | 0.95537 | 0.95434 | 0.9543 | 0.95465 | 0.95465 | 0.95309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89285 | 0.91499 | 0.9504
Gretna 33kV BB B |  |  |  | GRNA3B | GRNA3B | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9671 | 0.98529 | 0.98583 | 0.98949 | 0.98999 | 0.98286 | 0.98513 | 0.98717 | 0.99029 | 0.99022 | 0.99022 | 0.99018 | 0.99588 | 0.99588 | 0.99445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95358 | 0.97694 | 0.96922 | 0.98366 | 0.98125 | 0.99191
Middlebie 33/11kV T1 |  |  |  | MIBIT1 | MIBIT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0065 | 1.0181 | 0.98728 | 0.99392 | 1.0045 | 1.0053 | 0.99984 | 1.0015 | 0.99639 | 0.99801 | 0.99947 | 1.0017 | 1.0016 | 1.0016 | 1.0046 | 1.0043 | 1.0043 | 1.0033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96473 | 0.96473 | 0.96755 | 0.98635 | 0.98357 | 0.99676 | 0.99503 | 1.0013
Moffat 33/11kV T1 |  |  |  | MOFTT1 | MOFTT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88295 | 0.91322 | 0.94124 | 0.95014 | 0.94798 | 0.94794 | 0.9483 | 0.9483 | 0.94672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88126 | 0.90674 | 0.94403
Chapelcross 33kV BB A2 |  |  |  | CHAP3A2 | CHAP3A2 | 33 | 0 | 0 | 0 | 0 | 1.0275 | 1.0275 | 1.0219 | 1.0219 | 1.0212 | 1.0211 | 1.0234 | 1.0248 | 1.0248 | 1.0247 | 1.0274 | 1.0274 | 1.0231 | 1.0186 | 1.0132 | 1.0143 | 1.0204 | 1.0129 | 1.0086 | 1.0135 | 1.014 | 1.0066 | 1.0071 | 1.0001 | 1.0023 | 1.0043 | 1.0074 | 1.0073 | 1.0073 | 1.0073 | 1.0076 | 1.0076 | 1.0062 | 0 | 0 | 1.0187 | 1.0152 | 1.0161 | 1.0204 | 1.0243 | 0.98422 | 0.98033 | 0.98033 | 0.99573 | 1.0053 | 0.98674 | 1.0009 | 0.99855 | 1.0037
Chapelcross 33kV BB A1 |  |  |  | CHAP3A1 | CHAP3A1 | 33 | 0 | 0 | 0 | 0 | 1.0275 | 1.0275 | 1.0219 | 1.0219 | 1.0212 | 1.0211 | 1.0234 | 1.0248 | 1.0248 | 1.0247 | 1.0274 | 1.0274 | 1.0231 | 1.0186 | 1.0132 | 1.0143 | 1.0204 | 1.0129 | 1.0086 | 1.0135 | 1.014 | 1.0066 | 1.0071 | 1.0001 | 1.0023 | 1.0043 | 1.0074 | 1.0073 | 1.0073 | 1.0073 | 1.0076 | 1.0076 | 1.0062 | 0 | 0 | 1.0187 | 1.0152 | 1.0161 | 1.0204 | 1.0243 | 0.98422 | 0.98033 | 0.98033 | 0.99573 | 1.0053 | 0.98674 | 1.0009 | 0.99855 | 1.0037
Gretna 33/11kV T2 |  |  |  | GRNAT2 | GRNAT2 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9671 | 0.98529 | 0.98583 | 0.98949 | 0.98999 | 0.98286 | 0.98513 | 0.98717 | 0.99029 | 0.99022 | 0.99022 | 0.99018 | 0.99588 | 0.99588 | 0.99445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95358 | 0.97693 | 0.96922 | 0.98366 | 0.98125 | 0.99191
Newcastleton 11kV BB |  |  |  | NEWC5- | NEWC5- | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99366 | 0.99419 | 0.99264 | 0.99314 | 0.99186 | 0.9941 | 0.99613 | 0.99921 | 0.99914 | 0.99914 | 0.98946 | 1.0003 | 1.0003 | 0.99888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0004 | 0.99324 | 0.99265 | 0.99026 | 0.99629
Annan 33/11kV T2 |  |  |  | ANANT2 | ANANT2 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0066 | 1.0096 | 1.0175 | 1.01 | 1.0056 | 1.0106 | 1.0111 | 1.0037 | 1.0041 | 0.99716 | 0.99938 | 1.0014 | 1.0044 | 1.0044 | 1.0044 | 1.0043 | 1.0047 | 1.0047 | 1.0032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97734 | 0.97548 | 0.97548 | 0.99276 | 1.0024 | 0.98374 | 0.99794 | 0.99558 | 1.0007
Annan 11kV BB1 |  |  |  | ANAN5-1 | ANAN5-1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0151 | 1.0095 | 1.0158 | 1.0133 | 1.0179 | 1.0135 | 1.0185 | 1.019 | 1.0115 | 1.012 | 1.0049 | 1.0072 | 1.0092 | 1.0123 | 1.0122 | 1.0122 | 1.0122 | 1.0125 | 1.0125 | 1.0111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0042 | 1.0055 | 1.0055 | 1.0005 | 1.0102 | 1.0035 | 1.0057 | 1.0033 | 1.0085
Stevenscroft 33kV BB |  |  |  | STCR3- | STCR3- | 33 | 0 | 0 | 0 | 0.9958 | 1.0207 | 1.0207 | 1.0169 | 1.0169 | 1.0165 | 1.0164 | 1.0181 | 1.0191 | 1.0191 | 1.019 | 1.021 | 1.021 | 1.0179 | 1.0182 | 1.0173 | 1.019 | 1.0161 | 1.015 | 1.0144 | 1.0166 | 1.0159 | 1.0132 | 1.0114 | 1.0089 | 1.0105 | 1.0117 | 1.0128 | 1.0128 | 1.0128 | 1.0127 | 1.0129 | 1.0129 | 1.0136 | 1 | 1.0156 | 1.0156 | 1.0132 | 1.0141 | 1.0171 | 1.0199 | 0.9983 | 0.99658 | 0.99658 | 1.0062 | 1.0116 | 1.0031 | 1.0115 | 1.0104 | 1.013
Stevenscroft 11kV BB |  |  |  | STCR5- | STCR5- | 11 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Minsca 33kV WF BB |  |  |  | MINS0G | MINS0G | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 0 | 0 | 0 | 1.0089 | 1.0099 | 1.0142 | 1.0181 | 0.97766 | 0.97374 | 0.97374 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02
Ewe Hill |  |  |  | EWHC0G | EWHC0G | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.0098 | 1.0163 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 0 | 0 | 0 | 0 | 1.0119 | 1.0162 | 1.0201 | 0.97964 | 0.96009 | 0.96009 | 0.96293 | 0.98185 | 1.0101 | 1.02 | 1.02 | 1.02
Lockerbie 11kV BB A |  |  |  | LOBI5-1 | LOBI5-1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0001 | 1.0007 | 1.0075 | 1.0034 | 1.0022 | 1.0008 | 1.0102 | 1.0101 | 1.0101 | 1.0104 | 1.0104 | 1.0088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0049 | 1.0018 | 1.0092 | 1.0061
Kirkbank 11kV |  |  |  | KIBA5- | KIBA5- | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0017 | 0.99791 | 0.99242 | 1.0017 | 1.0006 | 1.0006 | 1.0009 | 1.0009 | 0.9993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9998 | 0.99098 | 0.99649
Gretna 11kB BB B |  |  |  | GRNA5-2 | GRNA5-2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0025 | 1.0013 | 1.0018 | 1.0087 | 1.0092 | 1.0019 | 1.0042 | 1.0063 | 1.0095 | 1.0094 | 1.0094 | 1.0094 | 1.0134 | 1.0134 | 1.0119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0009 | 1.0051 | 1.0001 | 1.0027 | 1.0002 | 1.0093
Lockerbie 11kV BB B |  |  |  | LOBI5-2 | LOBI5-2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0038 | 1.0115 | 1.0084 | 1.0096 | 1.0102 | 1.0101 | 1.0101 | 1.0104 | 1.0104 | 1.0088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0011 | 1.0095 | 1.0149 | 1.0061
Annan 11kV BB2 |  |  |  | ANAN5-2 | ANAN5-2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0094 | 1.0157 | 1.0133 | 1.0179 | 1.0135 | 1.0185 | 1.019 | 1.0115 | 1.012 | 1.0049 | 1.0072 | 1.0092 | 1.0123 | 1.0122 | 1.0122 | 1.0122 | 1.0125 | 1.0125 | 1.0111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0041 | 1.0054 | 1.0054 | 1.0005 | 1.0102 | 1.0035 | 1.0057 | 1.0033 | 1.0085
Moffat 11kV BB B |  |  |  | MOFT5-2 | MOFT5-2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0003 | 1.0008 | 0.99115 | 0.9971 | 0.99706 | 0.99743 | 0.99743 | 1.0086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99283 | 0.99292
Middlebie 11kV BB |  |  |  | MIBI5- | MIBI5- | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0054 | 1.0064 | 1.0006 | 0.99472 | 1.0054 | 1.0061 | 1.0006 | 1.0023 | 0.99719 | 0.99881 | 1.0003 | 1.0025 | 1.0025 | 1.0025 | 1.0054 | 1.0051 | 1.0051 | 1.0041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0012 | 1.0012 | 0.99314 | 0.99964 | 0.99682 | 0.99755 | 0.99583 | 1.0021
N/A |  |  |  | CRAG0A | CRAG0A | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94667 | 1.0074 | 1.0017 | 1.0025 | 1.0095 | 1.0115 | 1.0054 | 1.0073 | 1.0091 | 1.0117 | 1.0117 | 1.0117 | 1.0111 | 1.007 | 1.007 | 1.0057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9858 | 1.007 | 1.0036 | 1.0058 | 1.0038 | 1.0033
Langholm 11kV BB A |  |  |  | LAHO5-1 | LAHO5-1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94667 | 1.0074 | 1.0017 | 1.0025 | 1.0095 | 1.0115 | 1.0054 | 1.0073 | 1.0091 | 1.0117 | 1.0117 | 1.0117 | 1.0111 | 1.007 | 1.007 | 1.0057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9858 | 1.007 | 1.0036 | 1.0058 | 1.0038 | 1.0033
N/A |  |  |  | CRAG5A | CRAG5A | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94667 | 1.0074 | 1.0017 | 1.0025 | 1.0095 | 1.0115 | 1.0054 | 1.0073 | 1.0091 | 1.0117 | 1.0117 | 1.0117 | 1.0111 | 1.007 | 1.007 | 1.0057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9858 | 1.007 | 1.0036 | 1.0058 | 1.0038 | 1.0033
N/A |  |  |  | CRAG5B | CRAG5B | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94667 | 1.0074 | 1.0017 | 1.0025 | 1.0095 | 1.0115 | 1.0054 | 1.0073 | 1.0091 | 1.0117 | 1.0117 | 1.0117 | 1.0111 | 1.007 | 1.007 | 1.0057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9858 | 1.007 | 1.0036 | 1.0058 | 1.0038 | 1.0033
Ewehill 1 WF 33kV |  |  |  | EWEH3- | EWHC3- | 33 | 0 | 0 | 0 | 0 | 1.0306 | 1.0306 | 1.0251 | 1.0251 | 1.0217 | 1.0217 | 1.023 | 1.0238 | 1.0238 | 1.0237 | 1.0252 | 1.0252 | 1.0228 | 1.0203 | 1.0172 | 1.0095 | 1.021 | 0.99469 | 1.0013 | 1.0104 | 1.0115 | 1.0073 | 1.011 | 1.0071 | 1.0083 | 1.0094 | 1.0112 | 1.0111 | 1.0111 | 1.0134 | 1.0132 | 1.0132 | 1.0124 | 0 | 0 | 0 | 0 | 1.0153 | 1.0196 | 1.0235 | 0.98315 | 0.96367 | 0.96367 | 0.9665 | 0.98535 | 0.99451 | 1.0069 | 1.0056 | 1.0105
Gretna 11kB BB A |  |  |  | GRNA5-1 | GRNA5-1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0025 | 1.0013 | 1.0018 | 1.0087 | 1.0092 | 1.0019 | 1.0042 | 1.0063 | 1.0095 | 1.0094 | 1.0094 | 1.0094 | 1.0134 | 1.0134 | 1.0119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0009 | 1.0051 | 1.0001 | 1.0027 | 1.0002 | 1.0093
Moffat 11kV BB A |  |  |  | MOFT5-1 | MOFT5-1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9936 | 1.0021 | 0.99481 | 1.0043 | 0.9971 | 0.99706 | 0.99743 | 0.99743 | 1.0086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99168 | 0.99498 | 0.99292
Langholm 11kV BB A |  |  |  | LAHO5-2 | LAHO5-2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94667 | 1.0074 | 1.0017 | 1.0025 | 1.0095 | 1.0115 | 1.0054 | 1.0073 | 1.0091 | 1.0117 | 1.0117 | 1.0117 | 1.0111 | 1.007 | 1.007 | 1.0057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9858 | 1.007 | 1.0036 | 1.0058 | 1.0038 | 1.0033
Minsca 33kV BB |  |  |  | MINS3- | MINS3- | 33 | 0 | 0 | 0 | 0 | 1.0292 | 1.0292 | 1.0213 | 1.0213 | 1.021 | 1.021 | 1.0219 | 1.0225 | 1.0225 | 1.0225 | 1.0235 | 1.0235 | 1.0218 | 1.02 | 1.0179 | 1.0183 | 1.0223 | 1.0193 | 1.0176 | 1.0195 | 1.0201 | 1.0171 | 1.0187 | 1.016 | 1.0169 | 1.0177 | 1.0189 | 1.0188 | 1.0188 | 1.0188 | 1.0189 | 1.0189 | 1.0184 | 0 | 0 | 0 | 1.012 | 1.0129 | 1.0172 | 1.0211 | 0.98081 | 0.9769 | 0.9769 | 1.0149 | 1.0187 | 1.0113 | 1.0169 | 1.016 | 1.018
Lockerbie 33/11kV T1 |  |  |  | LOBIT1 | LOBIT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94167 | 0.94221 | 0.95512 | 0.94661 | 0.95811 | 0.96931 | 0.97791 | 0.97695 | 0.97691 | 0.97725 | 0.97725 | 0.97574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92033 | 0.94506 | 0.952 | 0.97311
N/A |  |  |  | CRAG0G | CRAG0G | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94667 | 1.0074 | 1.0017 | 1.0025 | 1.0095 | 1.0115 | 1.0054 | 1.0073 | 1.0091 | 1.0117 | 1.0117 | 1.0117 | 1.0111 | 1.007 | 1.007 | 1.0057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9858 | 1.007 | 1.0036 | 1.0058 | 1.0038 | 1.0033
Ewehill 1 WF 33kV BB |  |  |  | EWEH0G | EWHC0G | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.0098 | 1.0163 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.0191 | 1.0191 | 1.0191 | 1.0191 | 1.0191 | 0 | 1.0129 | 0.8781 | 0.87464 | 0.87464 | 0.88838 | 1.0111 | 0.88035 | 1.0066 | 0.89089 | 1.0094
Ewehill 1 WF 33kV WF BB |  |  |  | EWEH1Q | EWEH0G | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.0191 | 1.0191 | 1.0191 | 1.0191 | 1.0191 | 0 | 1.0129 | 0.8781 | 0.87464 | 0.87464 | 0.88838 | 1.0111 | 0.88035 | 1.0066 | 0.89089 | 1.0094
Ewehill 2 WF 33kV WF BB |  |  |  | EWEH0G_2 | EWEH0G | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.0191 | 1.0191 | 1.0191 | 1.0191 | 1.0191 | 0 | 1.013 | 0.79033 | 0.78721 | 0.78721 | 0.79957 | 0.99429 | 0.79235 | 0.9899 | 0.80184 | 0.99265
N/A |  |  |  | BR001- | BR001- | 132 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N/A |  |  |  | AL048A | AL048A | 132 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | 0 | 0 | 0 | 0 | 1.0063 | 1.0128 | 0.79021 | 0.78709 | 0.78709 | 0.79945 | 0.99414 | 0.79223 | 0.98975 | 0.80171 | 0.99249
N/A |  |  |  | AL048B | AL048B | 132 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | 0 | 0 | 0 | 0 | 0.014551 | 0.014646 | 0.011427 | 0.011382 | 0.011382 | 0.011561 | 0.014376 | 0.011457 | 0.014313 | 0.011594 | 0.014352
N/A |  |  |  | BV001A | BV001A | 132 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N/A |  |  |  | BV001B | BV001B | 132 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solway 33kV BB |  |  |  | SOLWAY | SOLWAY | 33 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gretna 400kV |  |  |  | GRTNA4- | GRTNA4- | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
End Of Sheet
Busbars on SLD
Transformers
Busbars N/A not on SLD
Busbars not shown
Not used
Vlookup
Copy and paste from PF
[5 empty] | PF Name | Nom Volt (kV)
[5 empty] | Terminal(4) | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0251 | 1.0217 | 1.0217 | 1.023 | 1.0238 | 1.0238 | 1.0237 | 1.0252 | 1.0252 | 1.0228 | 1.0203 | 1.0172 | 1.0095 | 1.021 | 0.99469 | 1.0013 | 1.0104 | 1.0115 | 1.0073 | 1.011 | 1.0071 | 1.0083 | 1.0094 | 1.0112 | 1.0111 | 1.0111 | 1.0134 | 1.0132 | 1.0132 | 1.0124
[5 empty] | LOBI3B | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93405 | 0.95738 | 0.96033 | 0.9737 | 0.96491 | 0.96583 | 0.96579 | 0.96613 | 0.96613 | 0.96467
[5 empty] | LOBIT2 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93405 | 0.95738 | 0.96033 | 0.9737 | 0.96491 | 0.96582 | 0.96578 | 0.96612 | 0.96612 | 0.96467
[5 empty] | LAHOT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84036 | 0.89454 | 0.94361 | 0.94437 | 0.93863 | 0.9404 | 0.93491 | 0.93665 | 0.93823 | 0.94063 | 0.94058 | 0.94058 | 0.9676 | 0.96389 | 0.96389 | 0.96276
[5 empty] | LAHOT2 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0038 | 1.0043 | 1 | 1.0005 | 0.99665 | 0.99888 | 1.0009 | 1.004 | 1.0039 | 1.0039 | 0.99426 | 0.99007 | 0.99007 | 0.98867
[5 empty] | GRNA3A | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0076 | 1.0081 | 1.003 | 1.0034 | 0.99867 | 1.0009 | 1.0029 | 1.006 | 1.0059 | 1.0059 | 0.99886 | 0.99021 | 0.99021 | 0.98879
[5 empty] | GRNA3B | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9671 | 0.98529 | 0.98583 | 0.98949 | 0.98999 | 0.98286 | 0.98513 | 0.98717 | 0.99029 | 0.99022 | 0.99022 | 0.99018 | 0.99588 | 0.99588 | 0.99445
[5 empty] | MOFTT2 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90082 | 0.94688 | 0.93779 | 0.93883 | 0.93878 | 0.93914 | 0.93914 | 0.93768
[5 empty] | GRNA5-1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0025 | 1.0013 | 1.0018 | 1.0087 | 1.0092 | 1.0019 | 1.0042 | 1.0063 | 1.0095 | 1.0094 | 1.0094 | 1.0094 | 1.0134 | 1.0134 | 1.0119
[5 empty] | LOBI5-1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0001 | 1.0007 | 1.0075 | 1.0034 | 1.0022 | 1.0008 | 1.0102 | 1.0101 | 1.0101 | 1.0104 | 1.0104 | 1.0088
[5 empty] | ANANT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.012 | 1.0066 | 1.0096 | 1.0175 | 1.01 | 1.0056 | 1.0106 | 1.0111 | 1.0037 | 1.0041 | 0.99716 | 0.99938 | 1.0014 | 1.0044 | 1.0044 | 1.0044 | 1.0043 | 1.0046 | 1.0046 | 1.0032
[5 empty] | ANANT2 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0066 | 1.0096 | 1.0175 | 1.01 | 1.0056 | 1.0106 | 1.0111 | 1.0037 | 1.0041 | 0.99716 | 0.99938 | 1.0014 | 1.0044 | 1.0044 | 1.0044 | 1.0043 | 1.0047 | 1.0047 | 1.0032
[5 empty] | LOBIT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94167 | 0.94221 | 0.95512 | 0.94661 | 0.95811 | 0.96931 | 0.97791 | 0.97695 | 0.97691 | 0.97725 | 0.97725 | 0.97574
[5 empty] | ANAN5-1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0151 | 1.0095 | 1.0158 | 1.0133 | 1.0179 | 1.0135 | 1.0185 | 1.019 | 1.0115 | 1.012 | 1.0049 | 1.0072 | 1.0092 | 1.0123 | 1.0122 | 1.0122 | 1.0122 | 1.0125 | 1.0125 | 1.0111
[5 empty] | CHAPX4 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90564 | 0.92921 | 0.9513 | 0.9601 | 0.95908 | 0.95903 | 0.95939 | 0.95939 | 0.95784
[5 empty] | LOBI3A | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94167 | 0.94221 | 0.95512 | 0.94661 | 0.95811 | 0.96931 | 0.9779 | 0.97695 | 0.9769 | 0.97725 | 0.97725 | 0.97574
[5 empty] | MOFT5-1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9936 | 1.0021 | 0.99481 | 1.0043 | 0.9971 | 0.99706 | 0.99743 | 0.99743 | 1.0086
[5 empty] | MOFTT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88295 | 0.91322 | 0.94124 | 0.95014 | 0.94798 | 0.94794 | 0.9483 | 0.9483 | 0.94672
[5 empty] | MIBI3- | 33 | 0 | 0 | 0 | 0 | 1.0299 | 1.0299 | 1.0244 | 1.0244 | 1.0221 | 1.0221 | 1.0238 | 1.0248 | 1.0248 | 1.0247 | 1.0266 | 1.0266 | 1.0235 | 1.0203 | 1.0164 | 1.0065 | 1.0181 | 0.98728 | 0.99392 | 1.0045 | 1.0053 | 0.99984 | 1.0015 | 0.99639 | 0.99801 | 0.99947 | 1.0017 | 1.0016 | 1.0016 | 1.0046 | 1.0043 | 1.0043 | 1.0033
[5 empty] | MINS3- | 33 | 0 | 0 | 0 | 0 | 1.0292 | 1.0292 | 1.0213 | 1.0213 | 1.021 | 1.021 | 1.0219 | 1.0225 | 1.0225 | 1.0225 | 1.0235 | 1.0235 | 1.0218 | 1.02 | 1.0179 | 1.0183 | 1.0223 | 1.0193 | 1.0176 | 1.0195 | 1.0201 | 1.0171 | 1.0187 | 1.016 | 1.0169 | 1.0177 | 1.0189 | 1.0188 | 1.0188 | 1.0188 | 1.0189 | 1.0189 | 1.0184
[5 empty] | ECCF1K | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | HAWI1- | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | GRNA4- | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0011 | 1.001
[5 empty] | GRNA1- | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0151 | 1.0148 | 1.1449 | 1.1449 | 1.0098 | 1.0074 | 1.0046 | 1.0052 | 1.0078 | 1.004 | 1.0017 | 1.0042 | 1.0043 | 1.0005 | 1.0007 | 0.99714 | 0.99828 | 0.99932 | 1.0009 | 1.0008 | 1.0008 | 1.0008 | 1.001 | 1.001 | 1.0032
[5 empty] | CRAG0A | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94667 | 1.0074 | 1.0017 | 1.0025 | 1.0095 | 1.0115 | 1.0054 | 1.0073 | 1.0091 | 1.0117 | 1.0117 | 1.0117 | 1.0111 | 1.007 | 1.007 | 1.0057
[5 empty] | STCR5- | 11 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[5 empty] | CHAPX3 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0071 | 1.0076 | 1.0024 | 1.0029 | 0.99815 | 1.0004 | 1.0024 | 1.0054 | 1.0054 | 1.0054 | 0.99834 | 0.99365 | 0.99365 | 0.99224
[5 empty] | LOBI5-2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0038 | 1.0115 | 1.0084 | 1.0096 | 1.0102 | 1.0101 | 1.0101 | 1.0104 | 1.0104 | 1.0088
[5 empty] | LAHO3B | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0038 | 1.0043 | 1 | 1.0005 | 0.99665 | 0.99888 | 1.0009 | 1.004 | 1.0039 | 1.0039 | 0.99426 | 0.99007 | 0.99007 | 0.98867
[5 empty] | MIBI5- | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0054 | 1.0064 | 1.0006 | 0.99472 | 1.0054 | 1.0061 | 1.0006 | 1.0023 | 0.99719 | 0.99881 | 1.0003 | 1.0025 | 1.0025 | 1.0025 | 1.0054 | 1.0051 | 1.0051 | 1.0041
[5 empty] | CRAG0G | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94667 | 1.0074 | 1.0017 | 1.0025 | 1.0095 | 1.0115 | 1.0054 | 1.0073 | 1.0091 | 1.0117 | 1.0117 | 1.0117 | 1.0111 | 1.007 | 1.007 | 1.0057
[5 empty] | CHAP3A1 | 33 | 0 | 0 | 0 | 0 | 1.0275 | 1.0275 | 1.0219 | 1.0219 | 1.0212 | 1.0211 | 1.0234 | 1.0248 | 1.0248 | 1.0247 | 1.0274 | 1.0274 | 1.0231 | 1.0186 | 1.0132 | 1.0143 | 1.0204 | 1.0129 | 1.0086 | 1.0135 | 1.014 | 1.0066 | 1.0071 | 1.0001 | 1.0023 | 1.0043 | 1.0074 | 1.0073 | 1.0073 | 1.0073 | 1.0076 | 1.0076 | 1.0062
[5 empty] | CHAP3A2 | 33 | 0 | 0 | 0 | 0 | 1.0275 | 1.0275 | 1.0219 | 1.0219 | 1.0212 | 1.0211 | 1.0234 | 1.0248 | 1.0248 | 1.0247 | 1.0274 | 1.0274 | 1.0231 | 1.0186 | 1.0132 | 1.0143 | 1.0204 | 1.0129 | 1.0086 | 1.0135 | 1.014 | 1.0066 | 1.0071 | 1.0001 | 1.0023 | 1.0043 | 1.0074 | 1.0073 | 1.0073 | 1.0073 | 1.0076 | 1.0076 | 1.0062
[5 empty] | LAHO3A | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84036 | 0.89454 | 0.94361 | 0.94437 | 0.93863 | 0.9404 | 0.93491 | 0.93665 | 0.93823 | 0.94063 | 0.94058 | 0.94058 | 0.9676 | 0.96389 | 0.96389 | 0.96276
[5 empty] | GRNAT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0076 | 1.0081 | 1.003 | 1.0034 | 0.99867 | 1.0009 | 1.0029 | 1.006 | 1.0059 | 1.0059 | 0.99886 | 0.99021 | 0.99021 | 0.98879
[5 empty] | GRNA5-2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0025 | 1.0013 | 1.0018 | 1.0087 | 1.0092 | 1.0019 | 1.0042 | 1.0063 | 1.0095 | 1.0094 | 1.0094 | 1.0094 | 1.0134 | 1.0134 | 1.0119
[5 empty] | CHAP1- | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0108 | 1.0149 | 1.0149 | 1.0146 | 1.1444 | 1.1444 | 1.0099 | 1.0074 | 1.0043 | 1.0049 | 1.0072 | 1.0029 | 1.0005 | 1.0032 | 1.0031 | 0.99895 | 0.99923 | 0.99531 | 0.99656 | 0.99769 | 0.99939 | 0.99935 | 0.99935 | 0.99933 | 0.99952 | 0.99952 | 1.0022
[5 empty] | MIBIT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0065 | 1.0181 | 0.98728 | 0.99392 | 1.0045 | 1.0053 | 0.99984 | 1.0015 | 0.99639 | 0.99801 | 0.99947 | 1.0017 | 1.0016 | 1.0016 | 1.0046 | 1.0043 | 1.0043 | 1.0033
[5 empty] | KIBA5- | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0017 | 0.99791 | 0.99242 | 1.0017 | 1.0006 | 1.0006 | 1.0009 | 1.0009 | 0.9993
[5 empty] | CRAG5B | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94667 | 1.0074 | 1.0017 | 1.0025 | 1.0095 | 1.0115 | 1.0054 | 1.0073 | 1.0091 | 1.0117 | 1.0117 | 1.0117 | 1.0111 | 1.007 | 1.007 | 1.0057
[5 empty] | NEWCT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99718 | 0.99771 | 0.9952 | 0.99569 | 0.99351 | 0.99575 | 0.99777 | 1.0008 | 1.0008 | 1.0008 | 0.99111 | 0.98691 | 0.98691 | 0.98551
[5 empty] | LAHO5-1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94667 | 1.0074 | 1.0017 | 1.0025 | 1.0095 | 1.0115 | 1.0054 | 1.0073 | 1.0091 | 1.0117 | 1.0117 | 1.0117 | 1.0111 | 1.007 | 1.007 | 1.0057
[5 empty] | MINS0G | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02
[5 empty] | ECCF1J | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | DUMF1- | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | LAHO5-2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94667 | 1.0074 | 1.0017 | 1.0025 | 1.0095 | 1.0115 | 1.0054 | 1.0073 | 1.0091 | 1.0117 | 1.0117 | 1.0117 | 1.0111 | 1.007 | 1.007 | 1.0057
[5 empty] | MOFT5-2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0003 | 1.0008 | 0.99115 | 0.9971 | 0.99706 | 0.99743 | 0.99743 | 1.0086
[5 empty] | Terminal(2) | 33 | 0 | 0 | 0 | 0 | 0 | 1.0292 | 1.0213 | 1.0213 | 1.021 | 1.021 | 1.0219 | 1.0225 | 1.0225 | 1.0225 | 1.0235 | 1.0235 | 1.0218 | 1.02 | 1.0179 | 1.0183 | 1.0223 | 1.0193 | 1.0176 | 1.0195 | 1.0201 | 1.0171 | 1.0187 | 1.016 | 1.0169 | 1.0177 | 1.0189 | 1.0188 | 1.0188 | 1.0188 | 1.0189 | 1.0189 | 1.0184
[5 empty] | EWHC0G | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.0098 | 1.0163 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02
[5 empty] | Terminal(3) | 33 | 0 | 0 | 0 | 0.9958 | 1.0207 | 1.0207 | 1.0169 | 1.0169 | 1.0165 | 1.0164 | 1.0181 | 1.0191 | 1.0191 | 1.019 | 1.021 | 1.021 | 1.0179 | 1.0182 | 1.0173 | 1.019 | 1.0161 | 1.015 | 1.0144 | 1.0166 | 1.0159 | 1.0132 | 1.0114 | 1.0089 | 1.0105 | 1.0117 | 1.0128 | 1.0128 | 1.0128 | 1.0127 | 1.0129 | 1.0129 | 1.0136
[5 empty] | NEWC5- | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99366 | 0.99419 | 0.99264 | 0.99314 | 0.99186 | 0.9941 | 0.99613 | 0.99921 | 0.99914 | 0.99914 | 0.98946 | 1.0003 | 1.0003 | 0.99888
[5 empty] | CHAPX1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0024 | 1.0029 | 0.99725 | 0.9987 | 1.0013 | 1.0049 | 1.0054 | 1.0053 | 1.0053 | 1.0056 | 1.0056 | 1.0042
[5 empty] | KIBAT1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89451 | 0.9214 | 0.94652 | 0.95537 | 0.95434 | 0.9543 | 0.95465 | 0.95465 | 0.95309
[5 empty] | EWEH1Q | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1451 | 1.1451 | 1.0092 | 1.0071 | 1.0046 | 1.0051 | 1.0081 | 1.0046 | 1.0026 | 1.0049 | 1.0051 | 1.0017 | 1.0019 | 0.9987 | 0.99972 | 1.0006 | 1.002 | 1.002 | 1.002 | 1.002 | 1.0021 | 1.0021 | 1.0041
[5 empty] | EWEH0G | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02
[5 empty] | EWHC3- | 33 | 0 | 0 | 0 | 0 | 1.0306 | 1.0306 | 1.0251 | 1.0251 | 1.0217 | 1.0217 | 1.023 | 1.0238 | 1.0238 | 1.0237 | 1.0252 | 1.0252 | 1.0228 | 1.0203 | 1.0172 | 1.0095 | 1.021 | 0.99469 | 1.0013 | 1.0104 | 1.0115 | 1.0073 | 1.011 | 1.0071 | 1.0083 | 1.0094 | 1.0112 | 1.0111 | 1.0111 | 1.0134 | 1.0132 | 1.0132 | 1.0124
[5 empty] | EWEH3- | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0104 | 1.0228 | 1.0218 | 1.0207 | 1.0209 | 1.0219 | 1.0203 | 1.0194 | 1.0204 | 1.0204 | 1.0188 | 1.0189 | 1.0175 | 1.018 | 1.0184 | 1.019 | 1.019 | 1.019 | 1.019 | 1.0191 | 1.0191 | 1.02
[5 empty] | GRNAT2 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9671 | 0.98529 | 0.98583 | 0.98949 | 0.98999 | 0.98286 | 0.98513 | 0.98717 | 0.99029 | 0.99022 | 0.99022 | 0.99018 | 0.99588 | 0.99588 | 0.99445
[5 empty] | CRAG5A | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94667 | 1.0074 | 1.0017 | 1.0025 | 1.0095 | 1.0115 | 1.0054 | 1.0073 | 1.0091 | 1.0117 | 1.0117 | 1.0117 | 1.0111 | 1.007 | 1.007 | 1.0057
[5 empty] | WYSB3- | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | ANAN5-2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0094 | 1.0157 | 1.0133 | 1.0179 | 1.0135 | 1.0185 | 1.019 | 1.0115 | 1.012 | 1.0049 | 1.0072 | 1.0092 | 1.0123 | 1.0122 | 1.0122 | 1.0122 | 1.0125 | 1.0125 | 1.0111
[5 empty] | STCR3- | 33 | 0 | 0 | 0 | 0.9958 | 1.0207 | 1.0207 | 1.0169 | 1.0169 | 1.0165 | 1.0164 | 1.0181 | 1.0191 | 1.0191 | 1.019 | 1.021 | 1.021 | 1.0179 | 1.0182 | 1.0173 | 1.019 | 1.0161 | 1.015 | 1.0144 | 1.0166 | 1.0159 | 1.0132 | 1.0114 | 1.0089 | 1.0105 | 1.0117 | 1.0128 | 1.0128 | 1.0128 | 1.0127 | 1.0129 | 1.0129 | 1.0136
Manual / calculated
[5 empty] | GRTNA4- | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1

## Transformers - Loading
Transformers - Loading
Results
Transformers
[7 empty] | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[7 empty] | Loading (%) >>> | [36 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  | Name | MVA | HV (kV) | LV (kV) | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  | EWHC3-_EWHC0G_1 | 13 | 33 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5923 | 4.574 | 6.0563 | 7.1495 | 7.1495 | 7.0675 | 9.2699 | 9.2699 | 5.836 | 3.7785 | 6.1234 | 18.1926 | 14.5081 | 28.5068 | 28.3242 | 21.0237 | 23.0502 | 27.7083 | 39.3562 | 42.0841 | 41.1214 | 40.3269 | 39.2614 | 39.2835 | 39.2833 | 38.1686 | 38.242 | 38.242 | 38.6115 | 0 | 0 | 0 | 0 | 6.6637 | 6.6356 | 6.6099 | 6.8831 | 7.0232 | 7.1166 | 7.0025 | 6.8676 | 42.1585 | 39.6089 | 40.8059 | 36.9253
|  |  | CRAG5A_CRAG0A_1 | 8.84 | 11 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.178e-07 | 1.2536e-07 | 1.2464e-07 | 1.2475e-07 | 1.2562e-07 | 1.2586e-07 | 1.2511e-07 | 1.2535e-07 | 1.2557e-07 | 1.259e-07 | 1.2589e-07 | 1.2589e-07 | 1.2582e-07 | 1.253e-07 | 1.253e-07 | 1.2514e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.107e-07 | 1.2267e-07 | 1.253e-07 | 1.2488e-07 | 1.2516e-07 | 1.2491e-07 | 1.2485e-07
|  |  | LAHOT2_LAHO20_T2 | 12 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2013e-08 | 9.2061e-08 | 9.4006e-08 | 9.1716e-08 | 9.3687e-08 | 9.3897e-08 | 9.1748e-08 | 9.2029e-08 | 9.2023e-08 | 9.2023e-08 | 23.4157 | 20.3913 | 20.3913 | 20.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3581e-08 | 9.4803e-08 | 9.3761e-08 | 9.3538e-08 | 20.7882
|  |  | CRAG5-_CRAG0B_1 | 2.66 | 11 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9177e-07 | 2.0457e-07 | 2.0336e-07 | 2.0353e-07 | 2.0501e-07 | 2.0543e-07 | 2.0415e-07 | 2.0455e-07 | 2.0492e-07 | 2.0548e-07 | 2.0547e-07 | 2.0547e-07 | 2.0535e-07 | 2.0448e-07 | 2.0448e-07 | 2.042e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7972e-07 | 2.0002e-07 | 2.0447e-07 | 2.0376e-07 | 2.0424e-07 | 2.0381e-07 | 2.0371e-07
|  |  | GRNAT2_GRNA20_T2 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.5333 | 93.4737 | 93.4215 | 61.8569 | 61.8254 | 62.2773 | 62.1329 | 62.0031 | 61.8065 | 61.811 | 61.8109 | 61.8134 | 41.3756 | 41.3756 | 41.4409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.3078 | 93.1148 | 62.385 | 62.2263 | 62.3804 | 41.5984
|  |  | MOFTT2_MOFT20_T2 | 7.5 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.639 | 30.1927 | 30.4866 | 34.0744 | 34.0759 | 34.063 | 34.063 | 34.1424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.1163 | 34.2173
|  |  | LOBIT2_LOBI20_T2 | 24 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.9727 | 48.5806 | 32.0878 | 31.6462 | 34.0293 | 33.6019 | 33.6031 | 33.5927 | 33.5927 | 33.6357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.05 | 31.6508 | 32.2889 | 33.7172
|  |  | GRNAT1_GRNA10_T1 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061342 | 0.061373 | 0.061059 | 0.061089 | 0.06229 | 0.060933 | 0.061056 | 0.061242 | 0.061238 | 0.061238 | 0.062302 | 20.3436 | 20.3436 | 20.3658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062333 | 0.061449 | 0.062338 | 0.062191 | 20.366
|  |  | MIBIT1_MIBI10_T1 | 10 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.2334 | 52.0682 | 53.0319 | 52.6777 | 52.1202 | 52.0832 | 52.3656 | 52.2796 | 52.547 | 52.4617 | 52.3849 | 52.2684 | 52.2711 | 52.271 | 52.1194 | 52.131 | 52.131 | 52.1851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.7528 | 82.5344 | 54.114 | 53.0818 | 53.232 | 52.5279 | 52.619 | 52.2901
|  |  | LAHOT1_LAHO10_T1 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.7843 | 90.2295 | 56.6345 | 56.5873 | 56.9238 | 56.8137 | 57.1562 | 57.0468 | 56.9485 | 56.7994 | 56.8027 | 56.8027 | 32.2512 | 35.5602 | 35.5602 | 35.6054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138.0996 | 93.4875 | 57.8194 | 58.0132 | 57.1318 | 57.2486 | 35.4709
|  |  | NEWCT1_NEWC10_T1 | 5 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.9322 | 43.9088 | 32.9829 | 32.9664 | 22.0059 | 21.9562 | 21.9116 | 21.844 | 21.8455 | 21.8455 | 22.0593 | 22.1524 | 22.1524 | 22.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.2991 | 22.3099 | 21.9884 | 22.0413 | 22.2417
|  |  | KIBAT1_KIBA10_T1 | 5 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.2482 | 44.613 | 28.967 | 28.6991 | 28.7301 | 28.7313 | 28.7206 | 28.7206 | 28.7676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.3616 | 44.9249 | 28.8488
|  |  | CHAP1-_CHAP3-_1 | 90 | 132 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036759 | 1.83 | 2.9668 | 2.9668 | 2.9006 | 4.9326 | 4.9326 | 1.6135 | 2.4009 | 3.3481 | 3.1605 | 8.1393 | 8.5169 | 8.8184 | 8.4826 | 10.3607 | 10.7877 | 10.7553 | 11.2904 | 11.1148 | 10.9657 | 10.7361 | 10.7406 | 10.7406 | 10.7431 | 10.7219 | 10.7219 | 5.5524 | 0 | 0 | 0 | 0 | 0 | 1.1195 | 2.1494 | 1.6869 | 1.6803 | 1.7101 | 1.7067 | 2.1269 | 1.6913 | 2.1175 | 1.7115 | 2.1234
|  |  | CHAP1-_CHAP3-_2 | 90 | 132 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | WYSB3-_WYSB0G_1 | 12.5 | 33 | 0.69 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | STCR3-_STCR5-_1 | 50 | 33 | 11 | 0 | 0 | 0 | 9.2225 | 17.1953 | 17.1953 | 15.7785 | 15.7785 | 16.2985 | 16.3331 | 17.1556 | 17.6828 | 17.6828 | 17.7396 | 18.8231 | 18.8231 | 17.1894 | 39.0621 | 63.389 | 72.9171 | 16.8257 | 44.9498 | 66.2116 | 55.1744 | 46.4539 | 69.0533 | 48.8358 | 71.2739 | 71.5203 | 68.994 | 59.5641 | 59.5861 | 59.5849 | 59.0499 | 59.142 | 59.142 | 75.3994 | 2.2e-08 | 10.3705 | 10.3705 | 8.9653 | 9.7783 | 11.7885 | 13.692 | 52.3528 | 61.7773 | 35.6476 | 50.9451 | 40.0843 | 83.7838 | 67.2917 | 72.8425 | 62.9666
|  |  | ANANT1_ANAN10_T1 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9873 | 104.5671 | 77.94 | 52.0869 | 51.8494 | 52.0755 | 51.8207 | 51.7941 | 52.1796 | 52.1541 | 52.5208 | 52.4036 | 52.2983 | 52.3927 | 52.3963 | 52.3962 | 52.3983 | 52.3811 | 52.3811 | 52.4556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.1168 | 78.7371 | 52.6469 | 52.7551 | 52.245 | 52.5963 | 52.4794 | 52.6044 | 52.5875
|  |  | ANANT2_ANAN20_T2 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5815 | 77.9443 | 52.0872 | 51.8497 | 52.0758 | 51.821 | 51.7944 | 52.1799 | 52.1544 | 52.5212 | 52.404 | 52.2987 | 51.8851 | 51.8887 | 51.8887 | 51.8907 | 51.8737 | 51.8737 | 51.9475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.1319 | 78.7418 | 52.6473 | 52.7555 | 52.2453 | 52.5967 | 52.4798 | 52.6049 | 52.078
|  |  | MINS3-_MINS0G_1 | 44.2 | 33 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 2.854 | 2.854 | 2.2916 | 2.2677 | 3.9685 | 5.0711 | 5.0711 | 4.9906 | 7.0766 | 7.0766 | 3.736 | 1.1093 | 4.4772 | 3.6555 | 16.0967 | 15.2335 | 15.783 | 15.2187 | 19.3248 | 19.9008 | 35.6379 | 36.2212 | 35.9453 | 35.7683 | 35.6318 | 35.6331 | 35.6331 | 35.6338 | 35.6282 | 35.6282 | 35.6661 | 0 | 0 | 0 | 6.1575 | 6.1516 | 6.1256 | 6.1019 | 6.3544 | 6.38 | 43.8064 | 44.0881 | 43.2629 | 45.9979 | 43.4815 | 43.711 | 43.3116
|  |  | LOBIT1_LOBI10_T1 | 24 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.0014 | 65.9611 | 48.4831 | 32.4533 | 32.0644 | 31.6948 | 30.5092 | 31.0905 | 31.0918 | 31.0806 | 31.0806 | 31.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.514 | 32.5072 | 32.2661 | 31.2143
|  |  | MOFTT1_MOFT10_T1 | 7.5 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.9324 | 47.0136 | 30.3745 | 30.0888 | 27.3447 | 27.3458 | 27.3364 | 27.3364 | 27.3703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.0582 | 47.3522 | 27.4521
|  |  | trf_EWEH1Q_EWEH3-_1 | 90 | 132 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033196 | 0.033196 | 2.3802 | 1.5824 | 0.62365 | 0.81334 | 8.4303 | 8.1744 | 8.1231 | 8.1861 | 10.2248 | 10.1613 | 10.1603 | 10.2433 | 10.2008 | 10.1753 | 10.16 | 10.16 | 10.16 | 10.1601 | 10.16 | 10.16 | 10.1905 | 0.03801 | 0.03801 | 0.03801 | 0.03801 | 0.03801 | 0 | 0.037781 | 0.036392 | 0.036248 | 0.036892 | 0.036817 | 0.038352 | 0.036485 | 0.038183 | 0.036921 | 0.038289
|  |  | trf_EWEH3-_EWEH0G_1 | 43.1667 | 33 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8344 | 3.1984 | 1.2319 | 1.6212 | 17.3345 | 16.8186 | 16.7181 | 16.8421 | 21.0223 | 20.8984 | 20.8959 | 21.0709 | 20.9823 | 20.9286 | 20.8951 | 20.8952 | 20.8952 | 20.8953 | 20.8949 | 20.8949 | 20.9538 | 2.5969e-08 | 2.5969e-08 | 2.5969e-08 | 2.5969e-08 | 2.5969e-08 | 0 | 2.5812e-08 | 2.2376e-08 | 2.2288e-08 | 2.2684e-08 | 2.2638e-08 | 2.5765e-08 | 2.2434e-08 | 2.5652e-08 | 2.2702e-08 | 2.5723e-08
|  |  | tr3_GRNA4-_GRNA1-_1 | 240 | 400 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035443 | 0.042453 | 0.042453 | 0.035268 | 0.035187 | 0.035089 | 0.035109 | 0.035201 | 0.035065 | 0.034987 | 0.035075 | 0.035077 | 0.034943 | 0.034952 | 0.025077 | 0.025106 | 0.025131 | 0.034957 | 0.034956 | 0.034956 | 0.034955 | 0.034961 | 0.034961 | 3.3993 | 17.0218 | 17.0218 | 17.0218 | 17.0218 | 17.0218 | 0 | 0.035375 | 0.019935 | 0.019856 | 0.020209 | 0.020168 | 0.024913 | 0.019986 | 0.024815 | 0.020225 | 0.024883
|  |  | tr3_GRNA4-_GRNA1-_2 | 240 | 400 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.5028 | 17.5028 | 17.5028 | 17.5028 | 17.5028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vlookup
Copy and paste from PF
|  |  | trf_EWEH3-_EWEH0G_1 | 43.1667 | 33 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8344 | 3.1984 | 1.2319 | 1.6212 | 17.3345 | 16.8186 | 16.7181 | 16.8421 | 21.0223 | 20.8984 | 20.8959 | 21.0709 | 20.9823 | 20.9286 | 20.8951 | 20.8952 | 20.8952 | 20.8953 | 20.8949 | 20.8949 | 20.9538
|  |  | trf_EWEH1Q_EWEH3-_1 | 90 | 132 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033196 | 0.033196 | 2.3802 | 1.5824 | 0.62365 | 0.81334 | 8.4303 | 8.1744 | 8.1231 | 8.1861 | 10.2248 | 10.1613 | 10.1603 | 10.2433 | 10.2008 | 10.1753 | 10.16 | 10.16 | 10.16 | 10.1601 | 10.16 | 10.16 | 10.1905
|  |  | EWHC3-_EWHC0G_1 | 13 | 33 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5923 | 4.574 | 6.0563 | 7.1495 | 7.1495 | 7.0675 | 9.2699 | 9.2699 | 5.836 | 3.7785 | 6.1234 | 18.1926 | 14.5081 | 28.5068 | 28.3242 | 21.0237 | 23.0502 | 27.7083 | 39.3562 | 42.0841 | 41.1214 | 40.3269 | 39.2614 | 39.2835 | 39.2833 | 38.1686 | 38.242 | 38.242 | 38.6115
|  |  | GRNAT2_GRNA20_T2 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.5333 | 93.4737 | 93.4215 | 61.8569 | 61.8254 | 62.2773 | 62.1329 | 62.0031 | 61.8065 | 61.811 | 61.8109 | 61.8134 | 41.3756 | 41.3756 | 41.4409
|  |  | LOBIT2_LOBI20_T2 | 24 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.9727 | 48.5806 | 32.0878 | 31.6462 | 34.0293 | 33.6019 | 33.6031 | 33.5927 | 33.5927 | 33.6357
|  |  | GRNAT1_GRNA10_T1 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061342 | 0.061373 | 0.061059 | 0.061089 | 0.06229 | 0.060933 | 0.061056 | 0.061242 | 0.061238 | 0.061238 | 0.062302 | 20.3436 | 20.3436 | 20.3658
|  |  | LAHOT1_LAHO10_T1 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.7843 | 90.2295 | 56.6345 | 56.5873 | 56.9238 | 56.8137 | 57.1562 | 57.0468 | 56.9485 | 56.7994 | 56.8027 | 56.8027 | 32.2512 | 35.5602 | 35.5602 | 35.6054
|  |  | ANANT1_ANAN10_T1 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9873 | 104.5671 | 77.94 | 52.0869 | 51.8494 | 52.0755 | 51.8207 | 51.7941 | 52.1796 | 52.1541 | 52.5208 | 52.4036 | 52.2983 | 52.3927 | 52.3963 | 52.3962 | 52.3983 | 52.3811 | 52.3811 | 52.4556
|  |  | NEWCT1_NEWC10_T1 | 5 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.9322 | 43.9088 | 32.9829 | 32.9664 | 22.0059 | 21.9562 | 21.9116 | 21.844 | 21.8455 | 21.8455 | 22.0593 | 22.1524 | 22.1524 | 22.184
|  |  | CHAP1-_CHAP3-_1 | 90 | 132 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036759 | 1.83 | 2.9668 | 2.9668 | 2.9006 | 4.9326 | 4.9326 | 1.6135 | 2.4009 | 3.3481 | 3.1605 | 8.1393 | 8.5169 | 8.8184 | 8.4826 | 10.3607 | 10.7877 | 10.7553 | 11.2904 | 11.1148 | 10.9657 | 10.7361 | 10.7406 | 10.7406 | 10.7431 | 10.7219 | 10.7219 | 5.5524
|  |  | MOFTT2_MOFT20_T2 | 7.5 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.639 | 30.1927 | 30.4866 | 34.0744 | 34.0759 | 34.063 | 34.063 | 34.1424
|  |  | LOBIT1_LOBI10_T1 | 24 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.0014 | 65.9611 | 48.4831 | 32.4533 | 32.0644 | 31.6948 | 30.5092 | 31.0905 | 31.0918 | 31.0806 | 31.0806 | 31.134
|  |  | MOFTT1_MOFT10_T1 | 7.5 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.9324 | 47.0136 | 30.3745 | 30.0888 | 27.3447 | 27.3458 | 27.3364 | 27.3364 | 27.3703
|  |  | LAHOT2_LAHO20_T2 | 12 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2013e-08 | 9.2061e-08 | 9.4006e-08 | 9.1716e-08 | 9.3687e-08 | 9.3897e-08 | 9.1748e-08 | 9.2029e-08 | 9.2023e-08 | 9.2023e-08 | 23.4157 | 20.3913 | 20.3913 | 20.451
|  |  | MIBIT1_MIBI10_T1 | 10 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.2334 | 52.0682 | 53.0319 | 52.6777 | 52.1202 | 52.0832 | 52.3656 | 52.2796 | 52.547 | 52.4617 | 52.3849 | 52.2684 | 52.2711 | 52.271 | 52.1194 | 52.131 | 52.131 | 52.1851
|  |  | ANANT2_ANAN20_T2 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5815 | 77.9443 | 52.0872 | 51.8497 | 52.0758 | 51.821 | 51.7944 | 52.1799 | 52.1544 | 52.5212 | 52.404 | 52.2987 | 51.8851 | 51.8887 | 51.8887 | 51.8907 | 51.8737 | 51.8737 | 51.9475
|  |  | KIBAT1_KIBA10_T1 | 5 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.2482 | 44.613 | 28.967 | 28.6991 | 28.7301 | 28.7313 | 28.7206 | 28.7206 | 28.7676
|  |  | CHAP1-_CHAP3-_2 | 90 | 132 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | CRAG5A_CRAG0A_1 | 8.84 | 11 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.178e-07 | 1.2536e-07 | 1.2464e-07 | 1.2475e-07 | 1.2562e-07 | 1.2586e-07 | 1.2511e-07 | 1.2535e-07 | 1.2557e-07 | 1.259e-07 | 1.2589e-07 | 1.2589e-07 | 1.2582e-07 | 1.253e-07 | 1.253e-07 | 1.2514e-07
|  |  | CRAG5-_CRAG0B_1 | 2.66 | 11 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9177e-07 | 2.0457e-07 | 2.0336e-07 | 2.0353e-07 | 2.0501e-07 | 2.0543e-07 | 2.0415e-07 | 2.0455e-07 | 2.0492e-07 | 2.0548e-07 | 2.0547e-07 | 2.0547e-07 | 2.0535e-07 | 2.0448e-07 | 2.0448e-07 | 2.042e-07
|  |  | STCR3-_STCR5-_1 | 50 | 33 | 11 | 0 | 0 | 0 | 9.2225 | 17.1953 | 17.1953 | 15.7785 | 15.7785 | 16.2985 | 16.3331 | 17.1556 | 17.6828 | 17.6828 | 17.7396 | 18.8231 | 18.8231 | 17.1894 | 39.0621 | 63.389 | 72.9171 | 16.8257 | 44.9498 | 66.2116 | 55.1744 | 46.4539 | 69.0533 | 48.8358 | 71.2739 | 71.5203 | 68.994 | 59.5641 | 59.5861 | 59.5849 | 59.0499 | 59.142 | 59.142 | 75.3994
|  |  | MINS3-_MINS0G_1 | 44.2 | 33 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 2.854 | 2.854 | 2.2916 | 2.2677 | 3.9685 | 5.0711 | 5.0711 | 4.9906 | 7.0766 | 7.0766 | 3.736 | 1.1093 | 4.4772 | 3.6555 | 16.0967 | 15.2335 | 15.783 | 15.2187 | 19.3248 | 19.9008 | 35.6379 | 36.2212 | 35.9453 | 35.7683 | 35.6318 | 35.6331 | 35.6331 | 35.6338 | 35.6282 | 35.6282 | 35.6661
|  |  | tr3_GRNA4-_GRNA1-_1 | 240 | 400 | 132.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035443 | 0.042453 | 0.042453 | 0.035268 | 0.035187 | 0.035089 | 0.035109 | 0.035201 | 0.035065 | 0.034987 | 0.035075 | 0.035077 | 0.034943 | 0.034952 | 0.025077 | 0.025106 | 0.025131 | 0.034957 | 0.034956 | 0.034956 | 0.034955 | 0.034961 | 0.034961 | 3.3993
|  |  | tr3_GRNA4-_GRNA1-_2 | 240 | 400 | 132.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual / calculated
End Of Sheet
Note on AA26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: cells in yellow: manual value

## Transformers - MVA
Transformers - MVA
Results
Transformers
[7 empty] | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[7 empty] | Loading (MVA) >>> | [36 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  | Name | MVA | HV (kV) | LV (kV) | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  | EWHC3-_EWHC0G_1 | 13 | 33 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60994 | 0.6075 | 0.80539 | 0.95152 | 0.95152 | 0.94054 | 1.2354 | 1.2354 | 0.77597 | 0.50116 | 0.80975 | 2.3874 | 1.9256 | 3.6862 | 3.6869 | 2.7615 | 3.0311 | 3.6285 | 5.1726 | 5.5095 | 5.3902 | 5.292 | 5.161 | 5.1637 | 5.1637 | 5.0284 | 5.0372 | 5.0372 | 5.0818 | 0 | 0 | 0 | 0 | 0.86629 | 0.86263 | 0.85929 | 0.8948 | 0.91302 | 0.92515 | 0.91033 | 0.89279 | 5.4806 | 5.1492 | 5.3048 | 4.8003
|  |  | CRAG5A_CRAG0A_1 | 8.84 | 11 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8581e-09 | 1.1164e-08 | 1.1037e-08 | 1.1055e-08 | 1.1211e-08 | 1.1254e-08 | 1.1119e-08 | 1.1162e-08 | 1.1201e-08 | 1.126e-08 | 1.1259e-08 | 1.1259e-08 | 1.1246e-08 | 1.1154e-08 | 1.1154e-08 | 1.1125e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.786e-09 | 1.0844e-08 | 1.1077e-08 | 1.104e-08 | 1.1064e-08 | 1.1042e-08 | 1.1037e-08
|  |  | LAHOT2_LAHO20_T2 | 12 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1083e-08 | 1.1095e-08 | 1.1281e-08 | 1.1012e-08 | 1.1205e-08 | 1.1255e-08 | 1.102e-08 | 1.1087e-08 | 1.1086e-08 | 1.1086e-08 | 2.7938 | 2.4227 | 2.4227 | 2.4263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.123e-08 | 1.1376e-08 | 1.1251e-08 | 1.1225e-08 | 2.4946
|  |  | CRAG5-_CRAG0B_1 | 2.66 | 11 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.658e-09 | 1.0964e-08 | 1.0837e-08 | 1.0855e-08 | 1.1011e-08 | 1.1054e-08 | 1.0919e-08 | 1.0962e-08 | 1.1001e-08 | 1.106e-08 | 1.1059e-08 | 1.1059e-08 | 1.1046e-08 | 1.0954e-08 | 1.0954e-08 | 1.0925e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7806e-09 | 5.3205e-09 | 5.439e-09 | 5.4201e-09 | 5.4327e-09 | 5.4212e-09 | 5.4186e-09
|  |  | GRNAT2_GRNA20_T2 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4524 | 10.7885 | 10.7883 | 7.1722 | 7.1722 | 7.1725 | 7.1724 | 7.1723 | 7.1722 | 7.1722 | 7.1722 | 7.1722 | 4.8309 | 4.8309 | 4.8315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.1569 | 11.1738 | 7.4862 | 7.4672 | 7.4856 | 4.9918
|  |  | MOFTT2_MOFT20_T2 | 7.5 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2995 | 2.1442 | 2.1443 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.4011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8087 | 2.5663
|  |  | LOBIT2_LOBI20_T2 | 24 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.0133 | 11.1624 | 7.3956 | 7.3954 | 7.8805 | 7.7888 | 7.7888 | 7.7891 | 7.7891 | 7.7874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.332 | 7.5962 | 7.7493 | 8.0921
|  |  | GRNAT1_GRNA10_T1 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007417 | 0.0074246 | 0.0073487 | 0.0073559 | 0.0074648 | 0.0073185 | 0.007348 | 0.0073929 | 0.0073919 | 0.0073919 | 0.0074677 | 2.3654 | 2.3654 | 2.3646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00748 | 0.0073739 | 0.0074806 | 0.0074629 | 2.4439
|  |  | MIBIT1_MIBI10_T1 | 10 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4911 | 5.2357 | 5.2357 | 5.2358 | 5.2357 | 5.2357 | 5.2357 | 5.2357 | 5.2358 | 5.2357 | 5.2357 | 5.2357 | 5.2357 | 5.2357 | 5.2357 | 5.2357 | 5.2357 | 5.2357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8753 | 8.2534 | 5.4114 | 5.3082 | 5.3232 | 5.2528 | 5.2619 | 5.229
|  |  | LAHOT1_LAHO10_T1 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.0878 | 9.6857 | 6.4129 | 6.4127 | 6.4116 | 6.4113 | 6.4123 | 6.412 | 6.4117 | 6.4113 | 6.4113 | 6.4113 | 3.7448 | 4.1131 | 4.1131 | 4.1136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.572 | 11.2185 | 6.9383 | 6.9616 | 6.8558 | 6.8698 | 4.2565
|  |  | NEWCT1_NEWC10_T1 | 5 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1904 | 2.1904 | 1.6412 | 1.6412 | 1.0932 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 1.0932 | 1.0931 | 1.0931 | 1.0931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.215 | 1.1155 | 1.0994 | 1.1021 | 1.1121
|  |  | KIBAT1_KIBA10_T1 | 5 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7394 | 2.0553 | 1.3709 | 1.3709 | 1.3709 | 1.3709 | 1.3709 | 1.3709 | 1.3709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0681 | 2.2462 | 1.4424
|  |  | CHAP1-_CHAP3-_1 | 90 | 132 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1092e-08 | 1.6648 | 2.7098 | 2.7098 | 2.6486 | 4.6363 | 4.6363 | 1.4666 | 2.1768 | 3.0263 | 2.8586 | 7.378 | 7.6876 | 7.9403 | 7.6591 | 9.354 | 9.6988 | 9.6723 | 10.1137 | 9.9689 | 9.8463 | 9.6567 | 9.6603 | 9.6603 | 9.6623 | 9.6451 | 9.6451 | 5.0084 | 0 | 0 | 0 | 0 | 0 | 1.0076 | 1.9344 | 1.5183 | 1.5123 | 1.5391 | 1.536 | 1.9143 | 1.5221 | 1.9058 | 1.5404 | 1.9111
|  |  | CHAP1-_CHAP3-_2 | 90 | 132 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | WYSB3-_WYSB0G_1 | 12.5 | 33 | 0.69 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875
|  |  | STCR3-_STCR5-_1 | 50 | 33 | 11 | 0 | 0 | 0 | 4.5919 | 8.7752 | 8.7752 | 8.0222 | 8.0222 | 8.2833 | 8.3008 | 8.7329 | 9.0102 | 9.0102 | 9.0387 | 9.6088 | 9.6088 | 8.7484 | 19.8862 | 32.2431 | 37.1514 | 8.5481 | 22.8119 | 33.5809 | 28.0448 | 23.5967 | 34.984 | 24.6962 | 35.9556 | 36.136 | 34.8993 | 30.1637 | 30.1735 | 30.1729 | 29.8995 | 29.9531 | 29.9531 | 38.2109 | 1.1e-08 | 5.1853 | 5.1853 | 4.4826 | 4.8892 | 5.8942 | 6.846 | 26.1764 | 30.8886 | 17.8238 | 25.4725 | 20.0421 | 41.8919 | 33.6459 | 36.4212 | 31.4833
|  |  | ANANT1_ANAN10_T1 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1789 | 12.1808 | 9.1085 | 6.0642 | 6.0642 | 6.0642 | 6.0641 | 6.0641 | 6.0642 | 6.0642 | 6.0643 | 6.0643 | 6.0643 | 6.0936 | 6.0936 | 6.0936 | 6.0936 | 6.0936 | 6.0936 | 6.0936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.614 | 9.4485 | 6.3176 | 6.3306 | 6.2694 | 6.3116 | 6.2975 | 6.3125 | 6.3105
|  |  | ANANT2_ANAN20_T2 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1823 | 9.1089 | 6.0643 | 6.0642 | 6.0643 | 6.0642 | 6.0642 | 6.0643 | 6.0643 | 6.0644 | 6.0644 | 6.0643 | 6.0349 | 6.0349 | 6.0349 | 6.0349 | 6.0349 | 6.0349 | 6.0349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6158 | 9.449 | 6.3177 | 6.3307 | 6.2694 | 6.3116 | 6.2976 | 6.3126 | 6.2494
|  |  | MINS3-_MINS0G_1 | 44.2 | 33 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2884 | 1.2884 | 1.0342 | 1.0234 | 1.7926 | 2.2919 | 2.2919 | 2.2554 | 3.2014 | 3.2014 | 1.6873 | 0.50011 | 2.0143 | 1.6453 | 7.2732 | 6.863 | 7.0985 | 6.8579 | 8.713 | 8.9469 | 16.0471 | 16.2657 | 16.1558 | 16.0887 | 16.0462 | 16.0464 | 16.0464 | 16.0465 | 16.046 | 16.046 | 16.0542 | 0 | 0 | 0 | 2.7216 | 2.719 | 2.7075 | 2.697 | 2.8086 | 2.82 | 19.3624 | 19.4869 | 19.1222 | 20.3311 | 19.2188 | 19.3203 | 19.1437
|  |  | LOBIT1_LOBI10_T1 | 24 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9163 | 14.9158 | 11.1138 | 7.3729 | 7.3731 | 7.3733 | 7.1604 | 7.2897 | 7.2897 | 7.2897 | 7.2897 | 7.2909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.2034 | 7.8017 | 7.7439 | 7.4914
|  |  | MOFTT1_MOFT10_T1 | 7.5 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2999 | 3.22 | 2.1442 | 2.1441 | 1.9442 | 1.9442 | 1.9442 | 1.9442 | 1.9434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8794 | 3.5514 | 2.0589
|  |  | trf_EWEH1Q_EWEH3-_1 | 90 | 132 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034212 | 0.034212 | 2.1619 | 1.4342 | 0.56387 | 0.73574 | 7.6488 | 7.391 | 7.33 | 7.4036 | 9.2491 | 9.1604 | 9.1615 | 9.207 | 9.1782 | 9.1636 | 9.1625 | 9.1623 | 9.1623 | 9.1621 | 9.1634 | 9.1634 | 9.2095 | 0.034209 | 0.034209 | 0.034209 | 0.034209 | 0.034209 | 0 | 0.034003 | 0.032753 | 0.032623 | 0.033203 | 0.033135 | 0.034517 | 0.032836 | 0.034364 | 0.033229 | 0.03446
|  |  | trf_EWEH3-_EWEH0G_1 | 43.1667 | 33 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1343 | 1.4108 | 0.54277 | 0.71444 | 7.6462 | 7.4074 | 7.3566 | 7.4186 | 9.2596 | 9.1911 | 9.1909 | 9.2549 | 9.2201 | 9.2003 | 9.1911 | 9.1911 | 9.1911 | 9.191 | 9.1914 | 9.1914 | 9.2256 | 1.121e-08 | 1.121e-08 | 1.121e-08 | 1.121e-08 | 1.121e-08 | 0 | 1.1142e-08 | 9.6592e-09 | 9.621e-09 | 9.792e-09 | 9.7721e-09 | 1.1122e-08 | 9.6839e-09 | 1.1073e-08 | 9.7998e-09 | 1.1104e-08
|  |  | tr3_GRNA4-_GRNA1-_1 | 240 | 400 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1899e-08 | 1.6081e-08 | 1.6081e-08 | 1.1782e-08 | 1.1728e-08 | 1.1663e-08 | 1.1676e-08 | 1.1737e-08 | 1.1647e-08 | 1.1595e-08 | 1.1654e-08 | 1.1655e-08 | 1.1566e-08 | 1.1572e-08 | 0.00011603 | 0.00011623 | 0.00011638 | 1.1575e-08 | 1.1575e-08 | 1.1575e-08 | 1.1574e-08 | 1.1578e-08 | 1.1578e-08 | 8.1282 | 40.8524 | 40.8524 | 40.8524 | 40.8524 | 40.8524 | 0 | 0.0849 | 0.047843 | 0.047654 | 0.048501 | 0.048403 | 0.059792 | 0.047966 | 0.059555 | 0.04854 | 0.059719
|  |  | tr3_GRNA4-_GRNA1-_2 | 240 | 400 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.0067 | 42.0067 | 42.0067 | 42.0067 | 42.0067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vlookup
Copy and paste from PF
|  |  | trf_EWEH3-_EWEH0G_1 | 43.1667 | 33 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1343 | 1.4108 | 0.54277 | 0.71444 | 7.6462 | 7.4074 | 7.3566 | 7.4186 | 9.2596 | 9.1911 | 9.1909 | 9.2549 | 9.2201 | 9.2003 | 9.1911 | 9.1911 | 9.1911 | 9.191 | 9.1914 | 9.1914 | 9.2256
|  |  | trf_EWEH1Q_EWEH3-_1 | 90 | 132 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034212 | 0.034212 | 2.1619 | 1.4342 | 0.56387 | 0.73574 | 7.6488 | 7.391 | 7.33 | 7.4036 | 9.2491 | 9.1604 | 9.1615 | 9.207 | 9.1782 | 9.1636 | 9.1625 | 9.1623 | 9.1623 | 9.1621 | 9.1634 | 9.1634 | 9.2095
|  |  | EWHC3-_EWHC0G_1 | 13 | 33 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60994 | 0.6075 | 0.80539 | 0.95152 | 0.95152 | 0.94054 | 1.2354 | 1.2354 | 0.77597 | 0.50116 | 0.80975 | 2.3874 | 1.9256 | 3.6862 | 3.6869 | 2.7615 | 3.0311 | 3.6285 | 5.1726 | 5.5095 | 5.3902 | 5.292 | 5.161 | 5.1637 | 5.1637 | 5.0284 | 5.0372 | 5.0372 | 5.0818
|  |  | GRNAT2_GRNA20_T2 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4524 | 10.7885 | 10.7883 | 7.1722 | 7.1722 | 7.1725 | 7.1724 | 7.1723 | 7.1722 | 7.1722 | 7.1722 | 7.1722 | 4.8309 | 4.8309 | 4.8315
|  |  | LOBIT2_LOBI20_T2 | 24 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.0133 | 11.1624 | 7.3956 | 7.3954 | 7.8805 | 7.7888 | 7.7888 | 7.7891 | 7.7891 | 7.7874
|  |  | GRNAT1_GRNA10_T1 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007417 | 0.0074246 | 0.0073487 | 0.0073559 | 0.0074648 | 0.0073185 | 0.007348 | 0.0073929 | 0.0073919 | 0.0073919 | 0.0074677 | 2.3654 | 2.3654 | 2.3646
|  |  | LAHOT1_LAHO10_T1 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.0878 | 9.6857 | 6.4129 | 6.4127 | 6.4116 | 6.4113 | 6.4123 | 6.412 | 6.4117 | 6.4113 | 6.4113 | 6.4113 | 3.7448 | 4.1131 | 4.1131 | 4.1136
|  |  | ANANT1_ANAN10_T1 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1789 | 12.1808 | 9.1085 | 6.0642 | 6.0642 | 6.0642 | 6.0641 | 6.0641 | 6.0642 | 6.0642 | 6.0643 | 6.0643 | 6.0643 | 6.0936 | 6.0936 | 6.0936 | 6.0936 | 6.0936 | 6.0936 | 6.0936
|  |  | NEWCT1_NEWC10_T1 | 5 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1904 | 2.1904 | 1.6412 | 1.6412 | 1.0932 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 1.0932 | 1.0931 | 1.0931 | 1.0931
|  |  | CHAP1-_CHAP3-_1 | 90 | 132 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1092e-08 | 1.6648 | 2.7098 | 2.7098 | 2.6486 | 4.6363 | 4.6363 | 1.4666 | 2.1768 | 3.0263 | 2.8586 | 7.378 | 7.6876 | 7.9403 | 7.6591 | 9.354 | 9.6988 | 9.6723 | 10.1137 | 9.9689 | 9.8463 | 9.6567 | 9.6603 | 9.6603 | 9.6623 | 9.6451 | 9.6451 | 5.0084
|  |  | MOFTT2_MOFT20_T2 | 7.5 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2995 | 2.1442 | 2.1443 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.4011
|  |  | LOBIT1_LOBI10_T1 | 24 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9163 | 14.9158 | 11.1138 | 7.3729 | 7.3731 | 7.3733 | 7.1604 | 7.2897 | 7.2897 | 7.2897 | 7.2897 | 7.2909
|  |  | MOFTT1_MOFT10_T1 | 7.5 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2999 | 3.22 | 2.1442 | 2.1441 | 1.9442 | 1.9442 | 1.9442 | 1.9442 | 1.9434
|  |  | LAHOT2_LAHO20_T2 | 12 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1083e-08 | 1.1095e-08 | 1.1281e-08 | 1.1012e-08 | 1.1205e-08 | 1.1255e-08 | 1.102e-08 | 1.1087e-08 | 1.1086e-08 | 1.1086e-08 | 2.7938 | 2.4227 | 2.4227 | 2.4263
|  |  | MIBIT1_MIBI10_T1 | 10 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4911 | 5.2357 | 5.2357 | 5.2358 | 5.2357 | 5.2357 | 5.2357 | 5.2357 | 5.2358 | 5.2357 | 5.2357 | 5.2357 | 5.2357 | 5.2357 | 5.2357 | 5.2357 | 5.2357 | 5.2357
|  |  | ANANT2_ANAN20_T2 | 12 | 33 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1823 | 9.1089 | 6.0643 | 6.0642 | 6.0643 | 6.0642 | 6.0642 | 6.0643 | 6.0643 | 6.0644 | 6.0644 | 6.0643 | 6.0349 | 6.0349 | 6.0349 | 6.0349 | 6.0349 | 6.0349 | 6.0349
|  |  | KIBAT1_KIBA10_T1 | 5 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7394 | 2.0553 | 1.3709 | 1.3709 | 1.3709 | 1.3709 | 1.3709 | 1.3709 | 1.3709
|  |  | CHAP1-_CHAP3-_2 | 90 | 132 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | CRAG5A_CRAG0A_1 | 8.84 | 11 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8581e-09 | 1.1164e-08 | 1.1037e-08 | 1.1055e-08 | 1.1211e-08 | 1.1254e-08 | 1.1119e-08 | 1.1162e-08 | 1.1201e-08 | 1.126e-08 | 1.1259e-08 | 1.1259e-08 | 1.1246e-08 | 1.1154e-08 | 1.1154e-08 | 1.1125e-08
|  |  | CRAG5-_CRAG0B_1 | 2.66 | 11 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.658e-09 | 1.0964e-08 | 1.0837e-08 | 1.0855e-08 | 1.1011e-08 | 1.1054e-08 | 1.0919e-08 | 1.0962e-08 | 1.1001e-08 | 1.106e-08 | 1.1059e-08 | 1.1059e-08 | 1.1046e-08 | 1.0954e-08 | 1.0954e-08 | 1.0925e-08
|  |  | STCR3-_STCR5-_1 | 50 | 33 | 11 | 0 | 0 | 0 | 4.5919 | 8.7752 | 8.7752 | 8.0222 | 8.0222 | 8.2833 | 8.3008 | 8.7329 | 9.0102 | 9.0102 | 9.0387 | 9.6088 | 9.6088 | 8.7484 | 19.8862 | 32.2431 | 37.1514 | 8.5481 | 22.8119 | 33.5809 | 28.0448 | 23.5967 | 34.984 | 24.6962 | 35.9556 | 36.136 | 34.8993 | 30.1637 | 30.1735 | 30.1729 | 29.8995 | 29.9531 | 29.9531 | 38.2109
|  |  | MINS3-_MINS0G_1 | 44.2 | 33 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2884 | 1.2884 | 1.0342 | 1.0234 | 1.7926 | 2.2919 | 2.2919 | 2.2554 | 3.2014 | 3.2014 | 1.6873 | 0.50011 | 2.0143 | 1.6453 | 7.2732 | 6.863 | 7.0985 | 6.8579 | 8.713 | 8.9469 | 16.0471 | 16.2657 | 16.1558 | 16.0887 | 16.0462 | 16.0464 | 16.0464 | 16.0465 | 16.046 | 16.046 | 16.0542
|  |  | tr3_GRNA4-_GRNA1-_1 | 240 | 400 | 132.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1899e-08 | 1.6081e-08 | 1.6081e-08 | 1.1782e-08 | 1.1728e-08 | 1.1663e-08 | 1.1676e-08 | 1.1737e-08 | 1.1647e-08 | 1.1595e-08 | 1.1654e-08 | 1.1655e-08 | 1.1566e-08 | 1.1572e-08 | 0.00011603 | 0.00011623 | 0.00011638 | 1.1575e-08 | 1.1575e-08 | 1.1575e-08 | 1.1574e-08 | 1.1578e-08 | 1.1578e-08 | 8.1282
|  |  | tr3_GRNA4-_GRNA1-_2 | 240 | 400 | 132.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual / calculated
End Of Sheet
Note on E30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: These two may need swopping around

## Transformers - MVar
Transformers - MVar
Results
Transformers
[7 empty] | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[7 empty] | Reactive Power (MVar) >>> | [36 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  | Name | MVA | HV (kV) | LV (kV) | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  | EWHC3-_EWHC0G_1 | 13 | 33 | 0.69 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0.86629 | 0.86263 | 0.85929 | 0.8948 | 0.91302 | 0.92515 | 0.91033 | 0.89279 | 5.4806 | 5.1492 | 5.3048 | 4.8003
|  |  | CRAG5A_CRAG0A_1 | 8.84 | 11 | 0.69 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.786e-09 | 1.0844e-08 | 1.1077e-08 | 1.104e-08 | 1.1064e-08 | 1.1042e-08 | 1.1037e-08
|  |  | LAHOT2_LAHO20_T2 | 12 | 33 | 11 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.123e-08 | 1.1376e-08 | 1.1251e-08 | 1.1225e-08 | 2.4946
|  |  | CRAG5-_CRAG0B_1 | 2.66 | 11 | 0.69 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7806e-09 | 5.3205e-09 | 5.439e-09 | 5.4201e-09 | 5.4327e-09 | 5.4212e-09 | 5.4186e-09
|  |  | GRNAT2_GRNA20_T2 | 12 | 33 | 11.5 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.1569 | 11.1738 | 7.4862 | 7.4672 | 7.4856 | 4.9918
|  |  | MOFTT2_MOFT20_T2 | 7.5 | 33 | 11.5 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8087 | 2.5663
|  |  | LOBIT2_LOBI20_T2 | 24 | 33 | 11.5 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.332 | 7.5962 | 7.7493 | 8.0921
|  |  | GRNAT1_GRNA10_T1 | 12 | 33 | 11.5 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00748 | 0.0073739 | 0.0074806 | 0.0074629 | 2.4439
|  |  | MIBIT1_MIBI10_T1 | 10 | 33 | 11 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8753 | 8.2534 | 5.4114 | 5.3082 | 5.3232 | 5.2528 | 5.2619 | 5.229
|  |  | LAHOT1_LAHO10_T1 | 12 | 33 | 11.5 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.572 | 11.2185 | 6.9383 | 6.9616 | 6.8558 | 6.8698 | 4.2565
|  |  | NEWCT1_NEWC10_T1 | 5 | 33 | 11 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.215 | 1.1155 | 1.0994 | 1.1021 | 1.1121
|  |  | KIBAT1_KIBA10_T1 | 5 | 33 | 11 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0681 | 2.2462 | 1.4424
|  |  | CHAP1-_CHAP3-_1 | 90 | 132 | 33 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 1.0076 | 1.9344 | 1.5183 | 1.5123 | 1.5391 | 1.536 | 1.9143 | 1.5221 | 1.9058 | 1.5404 | 1.9111
|  |  | CHAP1-_CHAP3-_2 | 90 | 132 | 33 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | WYSB3-_WYSB0G_1 | 12.5 | 33 | 0.69 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875 | 124.875
|  |  | STCR3-_STCR5-_1 | 50 | 33 | 11 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 1.1e-08 | 5.1853 | 5.1853 | 4.4826 | 4.8892 | 5.8942 | 6.846 | 26.1764 | 30.8886 | 17.8238 | 25.4725 | 20.0421 | 41.8919 | 33.6459 | 36.4212 | 31.4833
|  |  | ANANT1_ANAN10_T1 | 12 | 33 | 11.5 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.614 | 9.4485 | 6.3176 | 6.3306 | 6.2694 | 6.3116 | 6.2975 | 6.3125 | 6.3105
|  |  | ANANT2_ANAN20_T2 | 12 | 33 | 11.5 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6158 | 9.449 | 6.3177 | 6.3307 | 6.2694 | 6.3116 | 6.2976 | 6.3126 | 6.2494
|  |  | MINS3-_MINS0G_1 | 44.2 | 33 | 0.69 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 2.7216 | 2.719 | 2.7075 | 2.697 | 2.8086 | 2.82 | 19.3624 | 19.4869 | 19.1222 | 20.3311 | 19.2188 | 19.3203 | 19.1437
|  |  | LOBIT1_LOBI10_T1 | 24 | 33 | 11 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.2034 | 7.8017 | 7.7439 | 7.4914
|  |  | MOFTT1_MOFT10_T1 | 7.5 | 33 | 11.5 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8794 | 3.5514 | 2.0589
|  |  | trf_EWEH1Q_EWEH3-_1 | 90 | 132 | 33 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0.034209 | 0.034209 | 0.034209 | 0.034209 | 0.034209 | 0 | 0.034003 | 0.032753 | 0.032623 | 0.033203 | 0.033135 | 0.034517 | 0.032836 | 0.034364 | 0.033229 | 0.03446
|  |  | trf_EWEH3-_EWEH0G_1 | 43.1667 | 33 | 0.69 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 1.121e-08 | 1.121e-08 | 1.121e-08 | 1.121e-08 | 1.121e-08 | 0 | 1.1142e-08 | 9.6592e-09 | 9.621e-09 | 9.792e-09 | 9.7721e-09 | 1.1122e-08 | 9.6839e-09 | 1.1073e-08 | 9.7998e-09 | 1.1104e-08
|  |  | tr3_GRNA4-_GRNA1-_1 | 240 | 400 | 33 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 40.8524 | 40.8524 | 40.8524 | 40.8524 | 40.8524 | 0 | 0.0849 | 0.047843 | 0.047654 | 0.048501 | 0.048403 | 0.059792 | 0.047966 | 0.059555 | 0.04854 | 0.059719
|  |  | tr3_GRNA4-_GRNA1-_2 | 240 | 400 | 33 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 42.0067 | 42.0067 | 42.0067 | 42.0067 | 42.0067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vlookup
Copy and paste from PF
|  |  | trf_EWEH3-_EWEH0G_1 | 43.1667 | 33 | 0.69 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | trf_EWEH1Q_EWEH3-_1 | 90 | 132 | 33 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | EWHC3-_EWHC0G_1 | 13 | 33 | 0.69 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | GRNAT2_GRNA20_T2 | 12 | 33 | 11.5 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | LOBIT2_LOBI20_T2 | 24 | 33 | 11.5 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | GRNAT1_GRNA10_T1 | 12 | 33 | 11.5 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | LAHOT1_LAHO10_T1 | 12 | 33 | 11.5 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ANANT1_ANAN10_T1 | 12 | 33 | 11.5 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | NEWCT1_NEWC10_T1 | 5 | 33 | 11 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | CHAP1-_CHAP3-_1 | 90 | 132 | 33 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | MOFTT2_MOFT20_T2 | 7.5 | 33 | 11.5 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | LOBIT1_LOBI10_T1 | 24 | 33 | 11 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | MOFTT1_MOFT10_T1 | 7.5 | 33 | 11.5 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | LAHOT2_LAHO20_T2 | 12 | 33 | 11 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | MIBIT1_MIBI10_T1 | 10 | 33 | 11 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ANANT2_ANAN20_T2 | 12 | 33 | 11.5 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | KIBAT1_KIBA10_T1 | 5 | 33 | 11 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | CHAP1-_CHAP3-_2 | 90 | 132 | 33 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | CRAG5A_CRAG0A_1 | 8.84 | 11 | 0.69 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | CRAG5-_CRAG0B_1 | 2.66 | 11 | 0.69 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | STCR3-_STCR5-_1 | 50 | 33 | 11 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | MINS3-_MINS0G_1 | 44.2 | 33 | 0.69 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | tr3_GRNA4-_GRNA1-_1 | 240 | 400 | 132.57 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | tr3_GRNA4-_GRNA1-_2 | 240 | 400 | 132.57 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
Manual / calculated
End Of Sheet

## Transformers - Taps
Transformers - Taps
Results
Transformers
[8 empty] | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[8 empty] | Current Tap >>> | [36 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  | Name | HV (kV) | LV (kV) | Min Tap | Max Tap | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  | EWHC3-_EWHC0G_1 | 33 | 0.69 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | CRAG5A_CRAG0A_1 | 11 | 0.69 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | LAHOT2_LAHO20_T2 | 33 | 11 | 1 | 17 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 8 | 8 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 7 | 8 | 8 | 8
|  |  | CRAG5-_CRAG0B_1 | 11 | 0.69 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | GRNAT2_GRNA20_T2 | 33 | 11.5 | 1 | 17 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 9 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 10 | 10 | 11 | 11 | 11
|  |  | MOFTT2_MOFT20_T2 | 33 | 11.5 | 1 | 17 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 4 | 8 | 8 | 8 | 8 | 8 | 8 | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 4 | 8
|  |  | LOBIT2_LOBI20_T2 | 33 | 11.5 | 1 | 17 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 5 | 7 | 8 | 9 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 4 | 9 | 7 | 7
|  |  | GRNAT1_GRNA10_T1 | 33 | 11.5 | 1 | 17 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 11 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
|  |  | MIBIT1_MIBI10_T1 | 33 | 11 | 1 | 17 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 6 | 7 | 8 | 8 | 9 | 9 | 9
|  |  | LAHOT1_LAHO10_T1 | 33 | 11.5 | 1 | 17 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 1 | 2 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 1 | 1 | 5 | 5 | 6 | 6 | 8
|  |  | NEWCT1_NEWC10_T1 | 33 | 11 | -11 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | 0 | 0 | -1
|  |  | KIBAT1_KIBA10_T1 | 33 | 11 | -7 | 7 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -7 | -5 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -7 | -5 | -3
|  |  | CHAP1-_CHAP3-_1 | 132 | 33 | 1 | 19 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 1 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 19 | 19 | 19 | 19 | 8 | 19 | 8 | 19 | 8
|  |  | CHAP1-_CHAP3-_2 | 132 | 33 | 1 | 19 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  | WYSB3-_WYSB0G_1 | 33 | 0.69 | -2 | 2 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | STCR3-_STCR5-_1 | 33 | 11 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ANANT1_ANAN10_T1 | 33 | 11.5 | 1 | 17 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 12 | 12 | 12 | 11 | 12 | 12 | 12
|  |  | ANANT2_ANAN20_T2 | 33 | 11.5 | 1 | 17 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 12 | 12 | 12 | 11 | 12 | 12 | 12
|  |  | MINS3-_MINS0G_1 | 33 | 0.69 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | LOBIT1_LOBI10_T1 | 33 | 11 | 1 | 17 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 3 | 3 | 4 | 4 | 5 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 1 | 4 | 4 | 7
|  |  | MOFTT1_MOFT10_T1 | 33 | 11.5 | 1 | 17 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 3 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 3 | 5 | 8
|  |  | trf_EWEH1Q_EWEH3-_1 | 132 | 33 | 1 | 19 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 5 | 5 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 13 | 13 | 13 | 13 | 13 | 14 | 13 | 19 | 19 | 19 | 19 | 14 | 19 | 14 | 19 | 14
|  |  | trf_EWEH3-_EWEH0G_1 | 33 | 0.69 | -2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | tr3_GRNA4-_GRNA1-_1 | 400 | 33 | 1 | 15 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 15 | 15 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 1 | 1 | 1 | 13 | 13 | 13 | 13 | 13 | 13 | 11 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | tr3_GRNA4-_GRNA1-_2 | 400 | 33 | 1 | 15 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
Vlookup
Copy and paste from PF
|  |  | trf_EWEH3-_EWEH0G_1 | 33 | 0.69 | -2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | trf_EWEH1Q_EWEH3-_1 | 132 | 33 | 1 | 19 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 5 | 5 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
|  |  | EWHC3-_EWHC0G_1 | 33 | 0.69 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | GRNAT2_GRNA20_T2 | 33 | 11.5 | 1 | 17 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 9 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
|  |  | LOBIT2_LOBI20_T2 | 33 | 11.5 | 1 | 17 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 5 | 7 | 8 | 9 | 7 | 7 | 7 | 7 | 7 | 7
|  |  | GRNAT1_GRNA10_T1 | 33 | 11.5 | 1 | 17 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 11 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11
|  |  | LAHOT1_LAHO10_T1 | 33 | 11.5 | 1 | 17 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 1 | 2 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 8 | 8 | 8 | 8
|  |  | ANANT1_ANAN10_T1 | 33 | 11.5 | 1 | 17 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
|  |  | NEWCT1_NEWC10_T1 | 33 | 11 | -11 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1
|  |  | CHAP1-_CHAP3-_1 | 132 | 33 | 1 | 19 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 1 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  | MOFTT2_MOFT20_T2 | 33 | 11.5 | 1 | 17 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 4 | 8 | 8 | 8 | 8 | 8 | 8 | 7
|  |  | LOBIT1_LOBI10_T1 | 33 | 11 | 1 | 17 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 3 | 3 | 4 | 4 | 5 | 6 | 7 | 7 | 7 | 7 | 7 | 7
|  |  | MOFTT1_MOFT10_T1 | 33 | 11.5 | 1 | 17 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 3 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 7
|  |  | LAHOT2_LAHO20_T2 | 33 | 11 | 1 | 17 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 8 | 8 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 8
|  |  | MIBIT1_MIBI10_T1 | 33 | 11 | 1 | 17 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  |  | ANANT2_ANAN20_T2 | 33 | 11.5 | 1 | 17 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
|  |  | KIBAT1_KIBA10_T1 | 33 | 11 | -7 | 7 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -7 | -5 | -3 | -3 | -3 | -3 | -3 | -3 | -3
|  |  | CHAP1-_CHAP3-_2 | 132 | 33 | 1 | 19 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  | CRAG5A_CRAG0A_1 | 11 | 0.69 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | CRAG5-_CRAG0B_1 | 11 | 0.69 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | STCR3-_STCR5-_1 | 33 | 11 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MINS3-_MINS0G_1 | 33 | 0.69 | -2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | tr3_GRNA4-_GRNA1-_1 | 400 | 33 | 1 | 15 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 15 | 15 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 1 | 1 | 1 | 13 | 13 | 13 | 13 | 13 | 13 | 11
|  |  | tr3_GRNA4-_GRNA1-_2 | 400 | 33 | 1 | 15 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
End Of Sheet

## Lines - Loading
Lines - Loading
Results
Lines
[5 empty] | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[5 empty] | Loading (%) >>> | Value should be > 0 | [35 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  | network | Name | PF Name | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  | chapelcross33kv |  | lne_CHAP1-_HAKB1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | chapelcross33kv |  | CRAG5B_LAHO5-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9645e-07 | 4.224e-07 | 4.1994e-07 | 4.203e-07 | 4.233e-07 | 4.2413e-07 | 4.2154e-07 | 4.2237e-07 | 4.2311e-07 | 4.2424e-07 | 4.2422e-07 | 4.2422e-07 | 4.2398e-07 | 4.2221e-07 | 4.2221e-07 | 4.2165e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7206e-07 | 4.1317e-07 | 4.222e-07 | 4.2076e-07 | 4.2173e-07 | 4.2085e-07 | 4.2065e-07
|  | chapelcross33kv | CHAPX3_LAHO3B_1 | CHAPX3_LAHO3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9619 | 8.9571 | 6.7272 | 6.7238 | 4.488 | 4.4778 | 4.4687 | 4.455 | 4.4553 | 4.4553 | 15.9418 | 14.4643 | 14.4643 | 14.4978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0371 | 4.55 | 4.4844 | 4.4952 | 14.6709
|  | chapelcross33kv | LOBI3B_MOFTT2_1 | LOBI3B_MOFTT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.0381 | 20.5416 | 20.7353 | 23.4476 | 23.4486 | 23.4403 | 23.4403 | 23.4974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.3609 | 23.5393
|  | chapelcross33kv |  | lne_CHAP1-_DUMF1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | chapelcross33kv | CHAP3-_LOBI3B_1 | CHAP3-_LOBI3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.0539 | 55.8933 | 59.7408 | 47.1857 | 49.6274 | 49.9815 | 49.9835 | 49.9664 | 49.9664 | 50.0365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2934 | 36.4151 | 60.1453 | 50.1716
|  | chapelcross33kv |  | CHAP3-_CHAPX1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.3132 | 64.2739 | 47.243 | 63.7465 | 54.5431 | 45.9358 | 44.8291 | 44.2676 | 44.2695 | 44.2533 | 44.2533 | 44.3219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.7042 | 63.8171 | 54.8749 | 44.4616
|  | chapelcross33kv | CHAPX4_KIBAT1_1 | CHAPX4_KIBAT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.3125 | 12.6578 | 8.2912 | 8.2186 | 8.227 | 8.2274 | 8.2245 | 8.2245 | 8.2372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.344 | 12.7438 | 8.2592
|  | chapelcross33kv | CHAPX4_MOFTT1_1 | CHAPX4_MOFTT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3899 | 19.8314 | 12.8127 | 12.6921 | 11.5346 | 11.5351 | 11.5311 | 11.5311 | 11.5454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.443 | 19.9742 | 11.5799
|  | chapelcross33kv | CHAP3-_CHAPX3_1 | CHAP3-_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9832 | 8.9789 | 6.8585 | 6.8556 | 4.7962 | 4.7882 | 4.7817 | 4.7719 | 4.7721 | 4.7721 | 16.1306 | 24.3319 | 24.3319 | 24.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0544 | 4.8419 | 4.7936 | 4.8014 | 24.5514
|  | chapelcross33kv | GRNA3A_GRNAT1_1 | GRNA3A_GRNAT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00073684 | 0.00073722 | 0.00073344 | 0.0007338 | 0.00074822 | 0.00073193 | 0.0007334 | 0.00073564 | 0.00073559 | 0.00073559 | 0.00074837 | 0.23912 | 0.23912 | 0.23938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074875 | 0.00073813 | 0.00074881 | 0.00074704 | 0.23938
|  | chapelcross33kv | LOBI3A_LOBIT1_1 | LOBI3A_LOBIT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5856 | 1.5847 | 1.1648 | 0.77966 | 0.77032 | 0.76144 | 0.73295 | 0.74692 | 0.74695 | 0.74668 | 0.74668 | 0.74796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.622 | 0.78095 | 0.77516 | 0.74989
|  | chapelcross33kv |  | LAHO3A_LAHOT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.559 | 1.0838 | 0.68029 | 0.67973 | 0.68377 | 0.68245 | 0.68656 | 0.68525 | 0.68407 | 0.68227 | 0.68232 | 0.68231 | 0.3874 | 0.42715 | 0.42715 | 0.42769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6589 | 1.123 | 0.69453 | 0.69686 | 0.68627 | 0.68767 | 0.42608
|  | chapelcross33kv |  | LAHO3B_LAHOT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2105e-09 | 2.2117e-09 | 2.2304e-09 | 2.2034e-09 | 2.2228e-09 | 2.2277e-09 | 2.2042e-09 | 2.2109e-09 | 2.2108e-09 | 2.2108e-09 | 0.28127 | 0.24494 | 0.24494 | 0.24566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2203e-09 | 2.2213e-09 | 2.2245e-09 | 2.2192e-09 | 0.24971
|  | chapelcross33kv | MIBI3-_MIBIT1_1 | MIBI3-_MIBIT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0434 | 0.51477 | 0.53085 | 0.5273 | 0.52172 | 0.52135 | 0.52418 | 0.52332 | 0.526 | 0.52514 | 0.52437 | 0.52321 | 0.52323 | 0.52323 | 0.52172 | 0.52183 | 0.52183 | 0.52237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0886 | 0.82617 | 0.54168 | 0.53135 | 0.53285 | 0.5258 | 0.52672 | 0.52342
|  | chapelcross33kv | GRNA3B_GRNAT2_1 | GRNA3B_GRNAT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4959 | 1.0961 | 1.0954 | 0.72557 | 0.7252 | 0.73049 | 0.7288 | 0.72728 | 0.72498 | 0.72503 | 0.72503 | 0.72506 | 0.48557 | 0.48557 | 0.48634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5172 | 1.1053 | 0.74078 | 0.72989 | 0.7317 | 0.48818
|  | chapelcross33kv | MIBI3-_LAHO3A_1 | MIBI3-_LAHO3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140.4339 | 97.6333 | 61.2817 | 61.2306 | 61.5947 | 61.4756 | 61.8462 | 61.7278 | 61.6214 | 61.4601 | 61.4637 | 61.4637 | 34.8976 | 38.4782 | 38.4782 | 38.5271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149.4315 | 101.1587 | 62.5638 | 62.7735 | 61.8198 | 61.9462 | 38.3815
|  | chapelcross33kv | LAHO3B_NEWCT1_1 | LAHO3B_NEWCT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9793 | 8.9745 | 6.7414 | 6.738 | 4.4978 | 4.4876 | 4.4785 | 4.4647 | 4.465 | 4.465 | 4.5087 | 4.5277 | 4.5277 | 4.5342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0543 | 4.5599 | 4.4942 | 4.505 | 4.546
|  | chapelcross33kv | CHAP3-_MIBI3-_1 | CHAP3-_MIBI3-_1 | 0 | 0 | 0 | 0 | 5.0497 | 5.0497 | 5.0225 | 5.0225 | 4.1054 | 4.1218 | 3.1179 | 2.645 | 2.645 | 2.6735 | 2.3537 | 2.3537 | 3.2373 | 5.3831 | 8.3241 | 54.6248 | 16.336 | 88.0303 | 67.7202 | 49.2655 | 46.1577 | 47.4975 | 35.2022 | 36.6342 | 36.1344 | 35.7185 | 35.1511 | 35.163 | 35.1629 | 20.4476 | 22.3123 | 22.3123 | 22.5558 | 0 | 0 | 0 | 0 | 2.8311 | 2.8426 | 2.8535 | 2.7595 | 54.6199 | 119.9609 | 81.4607 | 60.7838 | 39.909 | 38.499 | 39.0634 | 24.9359
|  | chapelcross33kv | ANANT1_CHAP3-_1 | ANANT1_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.6894 | 58.0107 | 43.2479 | 28.57 | 28.7828 | 28.9079 | 28.7669 | 28.7521 | 28.9656 | 28.9515 | 29.1545 | 29.0896 | 29.0313 | 29.0838 | 29.0858 | 29.0857 | 29.0869 | 29.0774 | 29.0774 | 29.1186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.7552 | 44.7683 | 29.2243 | 29.2842 | 29.0018 | 29.5524 | 29.1316 | 29.2008 | 29.1916
|  | chapelcross33kv |  | CARU3A_CHAPX1_1 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38434 | 0.39013 | 0.38945 | 0.39186
|  | chapelcross33kv | ANANT2_CHAP3-_1 | ANANT2_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.0182 | 43.2501 | 28.5704 | 28.7831 | 28.9083 | 28.7672 | 28.7525 | 28.9659 | 28.9518 | 29.1549 | 29.09 | 29.0317 | 28.8025 | 28.8045 | 28.8045 | 28.8056 | 28.7962 | 28.7962 | 28.837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.7633 | 44.7707 | 29.2247 | 29.2846 | 29.0021 | 29.5527 | 29.132 | 29.2012 | 28.9093
|  | chapelcross33kv | EWEH3-_MIBI3-_1 | EWHC3-_MIBI3-_1 | 0 | 0 | 0 | 0 | 4.5998 | 4.5998 | 4.5751 | 4.5751 | 3.7397 | 3.7546 | 3.4381 | 4.0587 | 4.0587 | 4.0121 | 5.2624 | 5.2624 | 3.313 | 4.9035 | 7.5826 | 14.7565 | 8.7234 | 20.1084 | 20.0325 | 15.5142 | 16.0696 | 19.2309 | 24.167 | 26.2447 | 25.5433 | 24.9419 | 24.0882 | 24.1066 | 24.1064 | 23.1127 | 23.1835 | 23.1835 | 23.5258 | 0 | 0 | 0 | 0 | 3.7829 | 3.7669 | 3.7524 | 3.9074 | 3.987 | 4.04 | 3.9752 | 3.8986 | 26.6807 | 25.016 | 25.8453 | 23.0246
|  | chapelcross33kv |  | CRAG5A_LAHO5-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56623 | 0.60257 | 0.59913 | 0.59963 | 0.60383 | 0.605 | 0.60137 | 0.60253 | 0.60357 | 0.60515 | 0.60512 | 0.60512 | 0.60479 | 0.60231 | 0.60231 | 0.60152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53212 | 0.58964 | 0.6023 | 0.60028 | 0.60163 | 0.6004 | 0.60012
|  | chapelcross33kv | CHAPX4_LOBI3A_1 | CHAPX4_LOBI3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.4531 | 51.9847 | 33.8422 | 33.537 | 31.1273 | 31.1286 | 31.1173 | 31.1173 | 31.1552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5875 | 52.3481 | 31.2536
|  | chapelcross33kv | CHAPX1_LOBI3A_1 | CHAPX1_LOBI3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.3132 | 64.2739 | 47.243 | 63.7465 | 54.5431 | 45.9358 | 44.8291 | 44.2676 | 44.2695 | 44.2533 | 44.2533 | 44.3219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.7871 | 63.8599 | 54.9076 | 44.4463
|  | chapelcross33kv | CHAP3-_GRNA3B_1 | CHAP3-_GRNA3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.6616 | 44.4471 | 44.4223 | 29.4233 | 29.4083 | 29.6229 | 29.5543 | 29.4927 | 29.3994 | 29.4015 | 29.4015 | 29.4026 | 19.6909 | 19.6909 | 19.722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.526 | 44.8233 | 30.0403 | 29.5986 | 29.6718 | 19.7967
|  | chapelcross33kv | CHAP3-_MINS3-_1 | CHAP3-_MINS3-_1 | 0 | 0 | 0 | 0 | 4.9752 | 4.9752 | 3.1536 | 3.1536 | 2.9854 | 3.013 | 4.3852 | 5.6036 | 5.6036 | 5.5146 | 7.8196 | 7.8196 | 4.1283 | 5.1036 | 9.7824 | 8.85 | 17.7869 | 17.7014 | 19.2767 | 17.5499 | 21.5766 | 23.5989 | 39.6797 | 41.0494 | 40.5206 | 40.1171 | 39.6413 | 39.6502 | 39.6501 | 39.6551 | 39.6136 | 39.6136 | 39.808 | 0 | 0 | 0 | 6.804 | 6.7976 | 6.7688 | 6.7426 | 7.0216 | 7.0499 | 49.2415 | 49.72 | 47.9819 | 52.5142 | 48.6143 | 49.0691 | 48.1835
|  | chapelcross33kv | CHAP3-_STCR3-_1 | CHAP3-_STCR3-_1 | 0 | 0 | 0 | 0 | 5.1651 | 5.1651 | 4.4221 | 4.4221 | 4.4074 | 4.4087 | 4.7462 | 4.9562 | 4.9562 | 4.9543 | 5.3574 | 5.3574 | 4.7216 | 10.0908 | 17.4312 | 20.4019 | 4.4138 | 11.7402 | 18.2483 | 14.8933 | 12.2215 | 19.1098 | 12.8297 | 19.7321 | 19.8326 | 19.0656 | 16.1645 | 16.1704 | 16.1701 | 16.0032 | 16.0363 | 16.0363 | 21.0848 | 0 | 3.2408 | 3.2408 | 2.8017 | 3.0557 | 3.6839 | 4.2787 | 16.3602 | 19.3054 | 11.1399 | 15.9203 | 12.5263 | 26.1824 | 21.0287 | 22.7633 | 19.677
|  | chapelcross33kv | LOBI3B_LOBIT2_1 | LOBI3B_LOBIT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.609 | 1.1671 | 0.77088 | 0.76027 | 0.81752 | 0.80725 | 0.80728 | 0.80703 | 0.80703 | 0.80806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6348 | 0.76038 | 0.77571 | 0.81002
|  | chapelcross33kv | CHAP1-_GRNA1 | lne_AL048A_GRNA1-_1 | 11.3927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25653 | 0.25653 | 0.21915 | 1.0129 | 1.0129 | 0.84061 | 0.34666 | 0.51409 | 0.39702 | 5.0766 | 5.0228 | 5.0762 | 5.0193 | 6.2892 | 6.3604 | 6.3521 | 6.5233 | 6.4632 | 6.4165 | 6.3474 | 6.3485 | 6.3485 | 6.3491 | 6.3439 | 6.3439 | 1.9883 | 0 | 0 | 0 | 0 | 0 | 0.25431 | 0.89565 | 0.70492 | 0.70214 | 0.71461 | 0.71316 | 0.88967 | 0.70672 | 0.88572 | 0.71518 | 0.88817
|  | chapelcross33kv | CHAP1-_GRNA1 | lne_CHAP1-_AL048A_1 | 12.4386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76998 | 0.76998 | 0.72609 | 1.6571 | 1.6571 | 0.6399 | 0.39774 | 1.0441 | 0.91575 | 5.4978 | 5.5208 | 5.6238 | 5.5111 | 6.8727 | 7.0177 | 7.0048 | 7.2457 | 7.1635 | 7.0971 | 6.9972 | 6.999 | 6.999 | 6.9999 | 6.9917 | 6.9917 | 2.6106 | 0 | 0 | 0 | 0 | 0 | 0.76331 | 1.4655 | 1.1502 | 1.1456 | 1.166 | 1.1636 | 1.4502 | 1.1531 | 1.4438 | 1.1669 | 1.4478
|  | chapelcross33kv |  | lne_AL048B_GRNA1-_1 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | 0 | 0 | 0 | 0 | 0.003152 | 0.0031727 | 0.0024754 | 0.0024656 | 0.0025094 | 0.0025043 | 0.0031142 | 0.0024817 | 0.0031004 | 0.0025114 | 0.003109
|  | chapelcross33kv |  | lne_CHAP1-_AL048B_1 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | 0 | 0 | 0 | 0 | 0.0034395 | 0.003462 | 0.0027011 | 0.0026904 | 0.0027382 | 0.0027327 | 0.0033982 | 0.002708 | 0.0033832 | 0.0027404 | 0.0033925
|  | chapelcross33kv |  | CHAP08_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | chapelcross33kv | CHAP3-_SOLWAY | CHAP3-_SOLWAY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | chapelcross132kv | CHAP3A1 | CHAP3A1 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | chapelcross132kv | CHAP3A2 | CHAP3A2 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | chapelcross132kv | CHAP1-_CHAP3-_1 | CHAP1-_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | chapelcross132kv | CHAP1-_CHAP3-_2 | CHAP1-_CHAP3-_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | chapelcross132kv | CHAP1-_M1-_1 | CHAP1-_M1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | chapelcross132kv | CHAP1-_M1-_2 | CHAP1-_M1-_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | chapelcross132kv | CHAP1-_R1-_1 | CHAP1-_R1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | chapelcross132kv | HARK | HARK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | chapelcross132kv | DUMF-2 | DUMF-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | chapelcross132kv | ECCF-2 | ECCF-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | chapelcross132kv | GRNA-2 | GRNA-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | chapelcross132kv | DUMF-1 | DUMF-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | chapelcross132kv | ECCF-1 | ECCF-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | chapelcross132kv | CHAP1-_T1 | CHAP1-_T1 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | chapelcross132kv | CHAP1-_T2 | CHAP1-_T2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | chapelcross132kv | GRNA-1 | GRNA-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | stevenscroft33kv | STCR3- | STCR3- | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | stevenscroft33kv | STCR3-_STCR0G | STCR3-_STCR0G | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | stevenscroft33kv | STCR0G-_2 | STCR0G-_2 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | stevenscroft33kv | STCR0G-_1 | STCR0G-_1 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | stevenscroft33kv | STRC0G-_STCRLVT | STRC0G-_STCRLVT | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | stevenscroft33kv | STCR_AUX | STCR_AUX | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | stevenscroft33kv | STCR_DIESEL | STCR_DIESEL | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | minsca33kv | MINS3- | MINS3- | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | minsca33kv | MINS3-_MINSC | MINS3-_MINSC | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | minsca33kv | MINS0G | MINS0G | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | ewehillwindfarm1 | EWEH3- | EWEH3- | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | ewehillwindfarm1 | EWEH3-_EWEH0G_1 | EWHC3-_EWHC0G_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | ewehillwindfarm1 | EWEH0G | EWEH0G | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | gretna132kv | GRNA1-_SGT1 | GRNA1-_SGT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | gretna132kv | GRNA1-_SGT2 | GRNA1-_SGT2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | gretna132kv | GRNA1-_EWEH | GRNA1-_EWEH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | gretna400kv | GRNA4-_M1-_SGT1 | GRNA4-_M1-_SGT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | chapelcrossgretna1 | CHAP1-_GRNA1 | CHAP1-_GRNA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | ewehillgretna | EWEH3 | EWEH3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | ewehillgretna | EWEH3-_GRID1A-_WG2 | EWEH3-_GRID1A-_WG2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | ewehillwindfarm2 | EWEH0G_2 | EWEH0G_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  | gretna400kv | HARK4 | HARK4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999
|  | gretna400kv | GRNA4-_M1 | GRNA4-_M1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999
End of sheet
Lines are on SLD
Not used in simulation
Vlookup
Copy and paste from PF
|  |  |  | lne_CHAP1-_HAKB1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | lne_GRNA1-_JUNV1-_1 | 1.202e-12 | 1.202e-12 | 1.202e-12 | 1.202e-12 | 1.202e-12 | 1.202e-12 | 1.202e-12 | 1.202e-12 | 1.202e-12 | 1.202e-12 | 1.202e-12 | 1.202e-12 | 1.202e-12 | 1.202e-12 | 1.2022e-12 | 1.2022e-12 | 1.202e-12 | 1.202e-12 | 1.202e-12 | 1.202e-12 | 1.202e-12 | 1.202e-12 | 1.2024e-12 | 1.202e-12 | 1.202e-12 | 1.2022e-12 | 1.2024e-12 | 1.202e-12 | 1.2019e-12 | 1.2021e-12 | 1.2021e-12 | 1.2018e-12 | 1.2018e-12 | 1.202e-12 | 1.202e-12 | 1.2019e-12 | 1.2022e-12
|  |  |  | lne_CHAP1-_DUMF1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | MIBI3-_LAHO3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140.4339 | 97.6333 | 61.2817 | 61.2306 | 61.5947 | 61.4756 | 61.8462 | 61.7278 | 61.6214 | 61.4601 | 61.4637 | 61.4637 | 34.8976 | 38.4782 | 38.4782 | 38.5271
|  |  |  | CHAPX4_LOBI3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.4531 | 51.9847 | 33.8422 | 33.537 | 31.1273 | 31.1286 | 31.1173 | 31.1173 | 31.1552
|  |  |  | CHAP3-_GRNA3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.6616 | 44.4471 | 44.4223 | 29.4233 | 29.4083 | 29.6229 | 29.5543 | 29.4927 | 29.3994 | 29.4015 | 29.4015 | 29.4026 | 19.6909 | 19.6909 | 19.722
|  |  |  | CHAPX4_KIBAT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.3125 | 12.6578 | 8.2912 | 8.2186 | 8.227 | 8.2274 | 8.2245 | 8.2245 | 8.2372
|  |  |  | CHAPX4_MOFTT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3899 | 19.8314 | 12.8127 | 12.6921 | 11.5346 | 11.5351 | 11.5311 | 11.5311 | 11.5454
|  |  |  | LAHO3A_LAHOT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.559 | 1.0838 | 0.68029 | 0.67973 | 0.68377 | 0.68245 | 0.68656 | 0.68525 | 0.68407 | 0.68227 | 0.68232 | 0.68231 | 0.3874 | 0.42715 | 0.42715 | 0.42769
|  |  |  | MIBI3-_MIBIT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0434 | 0.51477 | 0.53085 | 0.5273 | 0.52172 | 0.52135 | 0.52418 | 0.52332 | 0.526 | 0.52514 | 0.52437 | 0.52321 | 0.52323 | 0.52323 | 0.52172 | 0.52183 | 0.52183 | 0.52237
|  |  |  | LAHO3B_LAHOT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2105e-09 | 2.2117e-09 | 2.2304e-09 | 2.2034e-09 | 2.2228e-09 | 2.2277e-09 | 2.2042e-09 | 2.2109e-09 | 2.2108e-09 | 2.2108e-09 | 0.28127 | 0.24494 | 0.24494 | 0.24566
|  |  |  | CHAPX3_LAHO3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9619 | 8.9571 | 6.7272 | 6.7238 | 4.488 | 4.4778 | 4.4687 | 4.455 | 4.4553 | 4.4553 | 15.9418 | 14.4643 | 14.4643 | 14.4978
|  |  |  | LAHO3B_NEWCT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9793 | 8.9745 | 6.7414 | 6.738 | 4.4978 | 4.4876 | 4.4785 | 4.4647 | 4.465 | 4.465 | 4.5087 | 4.5277 | 4.5277 | 4.5342
|  |  |  | LOBI3A_LOBIT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5856 | 1.5847 | 1.1648 | 0.77966 | 0.77032 | 0.76144 | 0.73295 | 0.74692 | 0.74695 | 0.74668 | 0.74668 | 0.74796
|  |  |  | LOBI3B_MOFTT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.0381 | 20.5416 | 20.7353 | 23.4476 | 23.4486 | 23.4403 | 23.4403 | 23.4974
|  |  |  | GRNA3B_GRNAT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4959 | 1.0961 | 1.0954 | 0.72557 | 0.7252 | 0.73049 | 0.7288 | 0.72728 | 0.72498 | 0.72503 | 0.72503 | 0.72506 | 0.48557 | 0.48557 | 0.48634
|  |  |  | LOBI3B_LOBIT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.609 | 1.1671 | 0.77088 | 0.76027 | 0.81752 | 0.80725 | 0.80728 | 0.80703 | 0.80703 | 0.80806
|  |  |  | CHAP3-_MIBI3-_1 | 0 | 0 | 0 | 0 | 5.0497 | 5.0497 | 5.0225 | 5.0225 | 4.1054 | 4.1218 | 3.1179 | 2.645 | 2.645 | 2.6735 | 2.3537 | 2.3537 | 3.2373 | 5.3831 | 8.3241 | 54.6248 | 16.336 | 88.0303 | 67.7202 | 49.2655 | 46.1577 | 47.4975 | 35.2022 | 36.6342 | 36.1344 | 35.7185 | 35.1511 | 35.163 | 35.1629 | 20.4476 | 22.3123 | 22.3123 | 22.5558
|  |  |  | CHAP3-_CHAPX1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.3132 | 64.2739 | 47.243 | 63.7465 | 54.5431 | 45.9358 | 44.8291 | 44.2676 | 44.2695 | 44.2533 | 44.2533 | 44.3219
|  |  |  | CHAP3-_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9832 | 8.9789 | 6.8585 | 6.8556 | 4.7962 | 4.7882 | 4.7817 | 4.7719 | 4.7721 | 4.7721 | 16.1306 | 24.3319 | 24.3319 | 24.377
|  |  |  | EWHC3-_MIBI3-_1 | 0 | 0 | 0 | 0 | 4.5998 | 4.5998 | 4.5751 | 4.5751 | 3.7397 | 3.7546 | 3.4381 | 4.0587 | 4.0587 | 4.0121 | 5.2624 | 5.2624 | 3.313 | 4.9035 | 7.5826 | 14.7565 | 8.7234 | 20.1084 | 20.0325 | 15.5142 | 16.0696 | 19.2309 | 24.167 | 26.2447 | 25.5433 | 24.9419 | 24.0882 | 24.1066 | 24.1064 | 23.1127 | 23.1835 | 23.1835 | 23.5258
|  |  |  | CHAP3-_LOBI3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.0539 | 55.8933 | 59.7408 | 47.1857 | 49.6274 | 49.9815 | 49.9835 | 49.9664 | 49.9664 | 50.0365
|  |  |  | GRNA3A_GRNAT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00073684 | 0.00073722 | 0.00073344 | 0.0007338 | 0.00074822 | 0.00073193 | 0.0007334 | 0.00073564 | 0.00073559 | 0.00073559 | 0.00074837 | 0.23912 | 0.23912 | 0.23938
|  |  |  | ANANT1_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.6894 | 58.0107 | 43.2479 | 28.57 | 28.7828 | 28.9079 | 28.7669 | 28.7521 | 28.9656 | 28.9515 | 29.1545 | 29.0896 | 29.0313 | 29.0838 | 29.0858 | 29.0857 | 29.0869 | 29.0774 | 29.0774 | 29.1186
|  |  |  | ANANT2_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.0182 | 43.2501 | 28.5704 | 28.7831 | 28.9083 | 28.7672 | 28.7525 | 28.9659 | 28.9518 | 29.1549 | 29.09 | 29.0317 | 28.8025 | 28.8045 | 28.8045 | 28.8056 | 28.7962 | 28.7962 | 28.837
|  |  |  | CHAPX1_LOBI3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.3132 | 64.2739 | 47.243 | 63.7465 | 54.5431 | 45.9358 | 44.8291 | 44.2676 | 44.2695 | 44.2533 | 44.2533 | 44.3219
|  |  |  | CRAG5A_LAHO5-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56623 | 0.60257 | 0.59913 | 0.59963 | 0.60383 | 0.605 | 0.60137 | 0.60253 | 0.60357 | 0.60515 | 0.60512 | 0.60512 | 0.60479 | 0.60231 | 0.60231 | 0.60152
|  |  |  | CRAG5B_LAHO5-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9645e-07 | 4.224e-07 | 4.1994e-07 | 4.203e-07 | 4.233e-07 | 4.2413e-07 | 4.2154e-07 | 4.2237e-07 | 4.2311e-07 | 4.2424e-07 | 4.2422e-07 | 4.2422e-07 | 4.2398e-07 | 4.2221e-07 | 4.2221e-07 | 4.2165e-07
|  |  |  | CHAP3-_STCR3-_1 | 0 | 0 | 0 | 0 | 5.1651 | 5.1651 | 4.4221 | 4.4221 | 4.4074 | 4.4087 | 4.7462 | 4.9562 | 4.9562 | 4.9543 | 5.3574 | 5.3574 | 4.7216 | 10.0908 | 17.4312 | 20.4019 | 4.4138 | 11.7402 | 18.2483 | 14.8933 | 12.2215 | 19.1098 | 12.8297 | 19.7321 | 19.8326 | 19.0656 | 16.1645 | 16.1704 | 16.1701 | 16.0032 | 16.0363 | 16.0363 | 21.0848
|  |  |  | CHAP3-_MINS3-_1 | 0 | 0 | 0 | 0 | 4.9752 | 4.9752 | 3.1536 | 3.1536 | 2.9854 | 3.013 | 4.3852 | 5.6036 | 5.6036 | 5.5146 | 7.8196 | 7.8196 | 4.1283 | 5.1036 | 9.7824 | 8.85 | 17.7869 | 17.7014 | 19.2767 | 17.5499 | 21.5766 | 23.5989 | 39.6797 | 41.0494 | 40.5206 | 40.1171 | 39.6413 | 39.6502 | 39.6501 | 39.6551 | 39.6136 | 39.6136 | 39.808
|  |  |  | lne_AL048A_GRNA1-_1 | 11.3927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25653 | 0.25653 | 0.21915 | 1.0129 | 1.0129 | 0.84061 | 0.34666 | 0.51409 | 0.39702 | 5.0766 | 5.0228 | 5.0762 | 5.0193 | 6.2892 | 6.3604 | 6.3521 | 6.5233 | 6.4632 | 6.4165 | 6.3474 | 6.3485 | 6.3485 | 6.3491 | 6.3439 | 6.3439 | 1.9883
|  |  |  | lne_CHAP1-_AL048A_1 | 12.4386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76998 | 0.76998 | 0.72609 | 1.6571 | 1.6571 | 0.6399 | 0.39774 | 1.0441 | 0.91575 | 5.4978 | 5.5208 | 5.6238 | 5.5111 | 6.8727 | 7.0177 | 7.0048 | 7.2457 | 7.1635 | 7.0971 | 6.9972 | 6.999 | 6.999 | 6.9999 | 6.9917 | 6.9917 | 2.6106
|  |  |  | lne_EWEH1S_EWEH1R_1 | 0.65526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75395 | 0.75395 | 1.5966 | 1.0485 | 0.38999 | 0.52026 | 5.7808 | 5.6109 | 5.5932 | 5.6186 | 7.0194 | 7.0053 | 6.999 | 7.135 | 7.0809 | 7.0405 | 6.9954 | 6.9962 | 6.9962 | 6.9966 | 6.9928 | 6.9928 | 6.9972
Manual/Calculated
|  |  |  | CHAP08_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | CHAP3-_SOLWAY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | CHAP3A1 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | CHAP3A2 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | CHAP1-_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | CHAP1-_CHAP3-_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | CHAP1-_M1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | CHAP1-_M1-_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | CHAP1-_R1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | HARK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DUMF-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | ECCF-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | GRNA-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | DUMF-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | ECCF-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | CHAP1-_T1 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | CHAP1-_T2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | GRNA-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | STCR3- | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | STCR3-_STCR0G | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | STCR0G-_2 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | STCR0G-_1 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | STRC0G-_STCRLVT | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | STCR_AUX | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | STCR_DIESEL | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | MINS3- | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | MINS3-_MINSC | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | MINS0G | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | EWEH3- | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | EWHC3-_EWHC0G_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | EWEH0G | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | GRNA1-_SGT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | GRNA1-_SGT2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | GRNA1-_EWEH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | GRNA4-_M1-_SGT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | CHAP1-_GRNA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | EWEH3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | EWEH3-_GRID1A-_WG2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | EWEH0G_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | HARK4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999
|  |  |  | GRNA4-_M1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999
Note on D9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 132kV line to Harker
Note on D15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: section of line from Chapelcross to T-off to Dumfries sector 414
Note on D21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Langholm 33kV A to Langholm T1
Note on D22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Langholm 33kV B to Langholm T2
Note on D29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Section of line between Chapelcross and Lockerbie going to Dumfries Sector 414
Note on D39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable section of 132kV line A from Chapelcross 132kV to Getna
Note on D40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable section of 132kV line A from Chapelcross 132kV to Getna
Note on D41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cable section of 132kV line B from Chapelcross 132kV to Getna
Note on D42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Overhead line B from Chapelcross 132kV to Getna
Note on D43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Gretna 33kV to T junction of line from Chapelcross to Langholm
Note on E43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Values beyond this point need to be calculated

## Lines - Current
Lines - Current
Results
Lines
[7 empty] | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[7 empty] | Current (kA) >>> | [36 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  | network | Name | PF Name | Rating (kA) | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  | chapelcross33kv |  | lne_CHAP1-_HAKB1-_1 | 0.57735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | chapelcross33kv |  | CRAG5B_LAHO5-_1 | 0.27293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.082e-09 | 1.1529e-09 | 1.1461e-09 | 1.1471e-09 | 1.1553e-09 | 1.1576e-09 | 1.1505e-09 | 1.1528e-09 | 1.1548e-09 | 1.1579e-09 | 1.1578e-09 | 1.1578e-09 | 1.1572e-09 | 1.1523e-09 | 1.1523e-09 | 1.1508e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0155e-09 | 1.1277e-09 | 1.1523e-09 | 1.1484e-09 | 1.151e-09 | 1.1486e-09 | 1.1481e-09
|  |  | chapelcross33kv | CHAPX3_LAHO3B_1 | CHAPX3_LAHO3B_1 | 0.42799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038324 | 0.038304 | 0.028772 | 0.028758 | 0.019206 | 0.019163 | 0.019124 | 0.019065 | 0.019067 | 0.019067 | 0.06823 | 0.061906 | 0.061906 | 0.062049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038678 | 0.019474 | 0.019193 | 0.019239 | 0.06279
|  |  | chapelcross33kv | LOBI3B_MOFTT2_1 | LOBI3B_MOFTT2_1 | 0.19402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08344 | 0.039856 | 0.040232 | 0.045494 | 0.045496 | 0.04548 | 0.04548 | 0.045591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.084131 | 0.045672
|  |  | chapelcross33kv |  | lne_CHAP1-_DUMF1-_1 | 0.74793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | chapelcross33kv | CHAP3-_LOBI3B_1 | CHAP3-_LOBI3B_1 | 0.36496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28095 | 0.20379 | 0.21791 | 0.17212 | 0.18086 | 0.18218 | 0.18219 | 0.18213 | 0.18213 | 0.18238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28574 | 0.1329 | 0.2195 | 0.1831
|  |  | chapelcross33kv |  | CHAP3-_CHAPX1_1 | 0.43091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27713 | 0.27696 | 0.20358 | 0.27469 | 0.23503 | 0.19794 | 0.19317 | 0.19076 | 0.19076 | 0.19069 | 0.19069 | 0.19099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28313 | 0.275 | 0.23646 | 0.19159
|  |  | chapelcross33kv | CHAPX4_KIBAT1_1 | CHAPX4_KIBAT1_1 | 0.31107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053854 | 0.039375 | 0.025791 | 0.025566 | 0.025592 | 0.025593 | 0.025584 | 0.025584 | 0.025623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053952 | 0.039642 | 0.025692
|  |  | chapelcross33kv | CHAPX4_MOFTT1_1 | CHAPX4_MOFTT1_1 | 0.31107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085202 | 0.061689 | 0.039856 | 0.039481 | 0.035881 | 0.035882 | 0.03587 | 0.03587 | 0.035914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085367 | 0.062134 | 0.036021
|  |  | chapelcross33kv | CHAP3-_CHAPX3_1 | CHAP3-_CHAPX3_1 | 0.43091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038404 | 0.038384 | 0.02896 | 0.028946 | 0.019577 | 0.019534 | 0.019498 | 0.019444 | 0.019445 | 0.019445 | 0.068757 | 0.10415 | 0.10415 | 0.10434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039017 | 0.020864 | 0.020656 | 0.02069 | 0.1058
|  |  | chapelcross33kv | GRNA3A_GRNAT1_1 | GRNA3A_GRNAT1_1 | 17.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00012878 | 0.00012885 | 0.00012819 | 0.00012825 | 0.00013077 | 0.00012793 | 0.00012818 | 0.00012858 | 0.00012857 | 0.00012857 | 0.0001308 | 0.041793 | 0.041793 | 0.041839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00013087 | 0.00012901 | 0.00013088 | 0.00013057 | 0.041839
|  |  | chapelcross33kv | LOBI3A_LOBIT1_1 | LOBI3A_LOBIT1_1 | 17.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27713 | 0.27696 | 0.20358 | 0.13627 | 0.13464 | 0.13308 | 0.12811 | 0.13055 | 0.13055 | 0.1305 | 0.1305 | 0.13073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28349 | 0.13649 | 0.13548 | 0.13107
|  |  | chapelcross33kv |  | LAHO3A_LAHOT1_1 | 17.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27248 | 0.18943 | 0.1189 | 0.1188 | 0.11951 | 0.11928 | 0.12 | 0.11977 | 0.11956 | 0.11925 | 0.11925 | 0.11925 | 0.06771 | 0.074657 | 0.074657 | 0.074752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28993 | 0.19627 | 0.12139 | 0.1218 | 0.11995 | 0.12019 | 0.07447
|  |  | chapelcross33kv |  | LAHO3B_LAHOT2_1 | 17.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8635e-10 | 3.8656e-10 | 3.8982e-10 | 3.8511e-10 | 3.885e-10 | 3.8937e-10 | 3.8524e-10 | 3.8642e-10 | 3.864e-10 | 3.864e-10 | 0.04916 | 0.042811 | 0.042811 | 0.042936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8806e-10 | 3.8824e-10 | 3.888e-10 | 3.8788e-10 | 0.043644
|  |  | chapelcross33kv | MIBI3-_MIBIT1_1 | MIBI3-_MIBIT1_1 | 17.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18236 | 0.089971 | 0.092782 | 0.092162 | 0.091187 | 0.091122 | 0.091616 | 0.091466 | 0.091933 | 0.091784 | 0.09165 | 0.091446 | 0.091451 | 0.091451 | 0.091185 | 0.091206 | 0.091206 | 0.0913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19027 | 0.1444 | 0.094675 | 0.092869 | 0.093132 | 0.0919 | 0.092059 | 0.091484
|  |  | chapelcross33kv | GRNA3B_GRNAT2_1 | GRNA3B_GRNAT2_1 | 17.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26145 | 0.19157 | 0.19146 | 0.12681 | 0.12675 | 0.12767 | 0.12738 | 0.12711 | 0.12671 | 0.12672 | 0.12672 | 0.12673 | 0.084868 | 0.084868 | 0.085002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26518 | 0.19319 | 0.12947 | 0.12757 | 0.12789 | 0.085324
|  |  | chapelcross33kv | MIBI3-_LAHO3A_1 | MIBI3-_LAHO3A_1 | 0.19402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27248 | 0.18943 | 0.1189 | 0.1188 | 0.11951 | 0.11928 | 0.12 | 0.11977 | 0.11956 | 0.11925 | 0.11925 | 0.11925 | 0.06771 | 0.074657 | 0.074657 | 0.074752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28993 | 0.19627 | 0.12139 | 0.1218 | 0.11995 | 0.12019 | 0.07447
|  |  | chapelcross33kv | LAHO3B_NEWCT1_1 | LAHO3B_NEWCT1_1 | 0.42799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038356 | 0.038336 | 0.028792 | 0.028777 | 0.019208 | 0.019165 | 0.019126 | 0.019067 | 0.019068 | 0.019068 | 0.019255 | 0.019336 | 0.019336 | 0.019364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038752 | 0.019516 | 0.019235 | 0.019281 | 0.019456
|  |  | chapelcross33kv | CHAP3-_MIBI3-_1 | CHAP3-_MIBI3-_1 | 0.36496 | 0 | 0 | 0 | 0 | 0.018429 | 0.018429 | 0.01833 | 0.01833 | 0.014983 | 0.015043 | 0.011379 | 0.0096531 | 0.0096531 | 0.0097571 | 0.0085901 | 0.0085901 | 0.011815 | 0.019646 | 0.030379 | 0.19936 | 0.059619 | 0.32127 | 0.24715 | 0.1798 | 0.16846 | 0.17334 | 0.12847 | 0.1337 | 0.13187 | 0.13036 | 0.12829 | 0.12833 | 0.12833 | 0.074625 | 0.08143 | 0.08143 | 0.082318 | 0 | 0 | 0 | 0 | 0.010332 | 0.010374 | 0.010414 | 0.010071 | 0.19934 | 0.4378 | 0.2973 | 0.22183 | 0.14565 | 0.1405 | 0.14256 | 0.091005
|  |  | chapelcross33kv | ANANT1_CHAP3-_1 | ANANT1_CHAP3-_1 | 0.36496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21054 | 0.21171 | 0.15783 | 0.10427 | 0.10504 | 0.1055 | 0.10499 | 0.10493 | 0.10571 | 0.10566 | 0.1064 | 0.10616 | 0.10595 | 0.10614 | 0.10615 | 0.10615 | 0.10615 | 0.10612 | 0.10612 | 0.10627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21808 | 0.16338 | 0.10666 | 0.10687 | 0.10584 | 0.10785 | 0.10632 | 0.10657 | 0.10654
|  |  | chapelcross33kv |  | CARU3A_CHAPX1_1 | 0.43091 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | -4.3048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016562 | 0.0016811 | 0.0016782 | 0.0016886
|  |  | chapelcross33kv | ANANT2_CHAP3-_1 | ANANT2_CHAP3-_1 | 0.36496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21174 | 0.15784 | 0.10427 | 0.10505 | 0.1055 | 0.10499 | 0.10493 | 0.10571 | 0.10566 | 0.1064 | 0.10617 | 0.10595 | 0.10512 | 0.10512 | 0.10512 | 0.10513 | 0.10509 | 0.10509 | 0.10524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21811 | 0.16339 | 0.10666 | 0.10688 | 0.10584 | 0.10785 | 0.10632 | 0.10657 | 0.10551
|  |  | chapelcross33kv | EWEH3-_MIBI3-_1 | EWHC3-_MIBI3-_1 | 0.40065 | 0 | 0 | 0 | 0 | 0.018429 | 0.018429 | 0.01833 | 0.01833 | 0.014983 | 0.015043 | 0.011379 | 0.0096531 | 0.0096531 | 0.0097571 | 0.0085901 | 0.0085901 | 0.011815 | 0.019646 | 0.030379 | 0.059121 | -0.03495 | -0.080564 | -0.08026 | -0.062157 | -0.064382 | -0.077048 | -0.096824 | -0.10515 | -0.10234 | -0.099929 | -0.096508 | -0.096582 | -0.096582 | -0.0926 | -0.092884 | -0.092884 | -0.094255 | 0 | 0 | 0 | 0 | 0.015156 | 0.015092 | 0.015034 | 0.015655 | 0.015974 | 0.016186 | 0.015927 | 0.01562 | 0.1069 | 0.10023 | 0.10355 | 0.092247
|  |  | chapelcross33kv |  | CRAG5A_LAHO5-_1 | 0.5616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0931e-09 | -1.1632e-09 | -1.1567e-09 | -1.1576e-09 | -1.1659e-09 | -1.1681e-09 | -1.1611e-09 | -1.1633e-09 | -1.1651e-09 | -1.1682e-09 | -1.1683e-09 | -1.1683e-09 | -1.1678e-09 | -1.163e-09 | -1.163e-09 | -1.1613e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029884 | 0.0033114 | 0.0033825 | 0.0033712 | 0.0033788 | 0.0033719 | 0.0033703
|  |  | chapelcross33kv | CHAPX4_LOBI3A_1 | CHAPX4_LOBI3A_1 | 0.19402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1386 | 0.10069 | 0.065307 | 0.064704 | 0.060368 | 0.06037 | 0.060348 | 0.060348 | 0.060426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1389 | 0.10157 | 0.06064
|  |  | chapelcross33kv | CHAPX1_LOBI3A_1 | CHAPX1_LOBI3A_1 | 0.43091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27713 | 0.27696 | 0.20358 | 0.27469 | 0.23503 | 0.19794 | 0.19317 | 0.19076 | 0.19076 | 0.19069 | 0.19069 | 0.19099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28349 | 0.27518 | 0.2366 | 0.19153
|  |  | chapelcross33kv | CHAP3-_GRNA3B_1 | CHAP3-_GRNA3B_1 | 0.431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26135 | 0.19151 | 0.1914 | 0.1268 | 0.12674 | 0.12766 | 0.12737 | 0.1271 | 0.1267 | 0.12671 | 0.12671 | 0.12671 | 0.084844 | 0.084844 | 0.084977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26518 | 0.19319 | 0.12947 | 0.12757 | 0.12789 | 0.085324
|  |  | chapelcross33kv | CHAP3-_MINS3-_1 | CHAP3-_MINS3-_1 | 0.69982 | 0 | 0 | 0 | 0 | 0.034818 | 0.034818 | 0.016622 | 0.016622 | 0.020892 | 0.021085 | 0.0099902 | 0.0092886 | 0.0092886 | 0.0090604 | 0.021142 | 0.021142 | 0.011072 | 0.035716 | 0.068459 | 0.061934 | -0.11735 | -0.12388 | -0.1349 | -0.12282 | -0.151 | -0.16515 | -0.27769 | -0.28727 | -0.28357 | -0.28075 | -0.27742 | -0.27748 | -0.27748 | -0.27751 | -0.27722 | -0.27722 | -0.27858 | 0 | 0 | 0 | 0.047616 | 0.047571 | 0.04737 | 0.047186 | 0.049138 | 0.049337 | 0.3446 | 0.34795 | 0.33579 | 0.3675 | 0.34021 | 0.34339 | 0.3372
|  |  | chapelcross33kv | CHAP3-_STCR3-_1 | CHAP3-_STCR3-_1 | 2.7993 | 0 | 0 | 0 | 0 | -0.053247 | -0.053247 | -0.033691 | -0.033691 | -0.035721 | -0.035933 | -0.04432 | -0.049714 | -0.049714 | -0.049924 | -0.060604 | -0.060604 | -0.044158 | -0.24139 | -0.45788 | -0.54077 | -0.039308 | -0.2966 | -0.48423 | -0.38593 | -0.30922 | -0.50968 | -0.33376 | -0.53127 | -0.53261 | -0.50998 | -0.42686 | -0.42709 | -0.42707 | -0.42244 | -0.4231 | -0.4231 | -0.56499 | 0.090719 | 0 | 0.090719 | 0.078426 | 0.085538 | 0.10312 | 0.11977 | 0.45797 | 0.54041 | 0.31184 | 0.44565 | 0.35065 | 0.73292 | 0.58865 | 0.63721 | 0.55081
|  |  | chapelcross33kv | LOBI3B_LOBIT2_1 | LOBI3B_LOBIT2_1 | 17.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28121 | 0.20399 | 0.13473 | 0.13288 | 0.14289 | 0.14109 | 0.1411 | 0.14105 | 0.14105 | 0.14123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28574 | 0.1329 | 0.13558 | 0.14158
|  |  | chapelcross33kv | CHAP1-_GRNA1 | lne_AL048A_GRNA1-_1 | 0.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016161 | 0.0016161 | 0.0013806 | 0.0063813 | 0.0063813 | 0.0036945 | 0.00066951 | 0.0032387 | 0.0025012 | -0.031741 | -0.031644 | -0.03198 | -0.031621 | -0.039588 | -0.04007 | -0.040018 | -0.041097 | -0.040718 | -0.040424 | -0.039988 | -0.039995 | -0.039995 | -0.039999 | -0.039967 | -0.039967 | -0.012527 | 0 | 0 | 0 | 0 | 0 | 0.0016021 | 0.0056426 | 0.004441 | 0.0044235 | 0.004502 | 0.0044929 | 0.0056049 | 0.0044524 | 0.00558 | 0.0045056 | 0.0055955
|  |  | chapelcross33kv | CHAP1-_GRNA1 | lne_CHAP1-_AL048A_1 | 0.57735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044455 | 0.0044455 | 0.0041921 | 0.0095675 | 0.0095675 | 0.00094379 | 0.0022964 | 0.0060281 | 0.0052871 | -0.03151 | -0.031874 | -0.032469 | -0.031818 | -0.039679 | -0.040517 | -0.040442 | -0.041833 | -0.041359 | -0.040975 | -0.040398 | -0.040409 | -0.040408 | -0.040414 | -0.040366 | -0.040366 | -0.015072 | 0 | 0 | 0 | 0 | 0 | 0.004407 | 0.0084609 | 0.0066406 | 0.0066144 | 0.0067319 | 0.0067183 | 0.0083727 | 0.0066576 | 0.0083356 | 0.0067373 | 0.0083587
|  |  | chapelcross33kv |  | lne_AL048B_GRNA1-_1 | 0.63 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | -6.2937 | 0 | 0 | 0 | 1.9858e-05 | 1.9988e-05 | 1.5595e-05 | 1.5533e-05 | 1.5809e-05 | 1.5777e-05 | 1.9619e-05 | 1.5635e-05 | 1.9533e-05 | 1.5822e-05 | 1.9587e-05
|  |  | chapelcross33kv |  | lne_CHAP1-_AL048B_1 | 0.5773 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | -5.7672 | 0 | 0 | 0 | 1.9856e-05 | 1.9986e-05 | 1.5593e-05 | 1.5532e-05 | 1.5808e-05 | 1.5776e-05 | 1.9618e-05 | 1.5633e-05 | 1.9531e-05 | 1.582e-05 | 1.9585e-05
|  |  | chapelcross33kv |  | CHAP08_CHAPX3_1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross33kv | CHAP3-_SOLWAY | CHAP3-_SOLWAY | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | CHAP3A1 | CHAP3A1 | 999 | 0 | 0 | 0 | 0 | 1.2491e-08 | 1.2491e-08 | 0.001261 | 0.001261 | 0.00015406 | 0.00019476 | -0.022951 | -0.030772 | -0.030772 | -0.031106 | -0.030873 | -0.030873 | -0.021271 | 0.02451 | 0.064405 | 0.036195 | 0.1115 | 0.11089 | 0.10037 | 0.072535 | 0.1095 | 0.11388 | 0.13205 | 0.14015 | 0.13387 | 0.21502 | 0.17188 | 0.17601 | 0.18019 | 0.13111 | 0.095463 | 0.095463 | -0.0458 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | CHAP3A2 | CHAP3A2 | 999 | 0 | 0 | 0 | 0 | 1.2491e-08 | 1.2491e-08 | 0.001261 | 0.001261 | 0.00015406 | 0.00019476 | -0.022951 | -0.030772 | -0.030772 | -0.031106 | -0.030873 | -0.030873 | -0.021271 | 0.02451 | 0.064405 | 0.036195 | 0.1115 | 0.11089 | 0.10037 | 0.072535 | 0.1095 | 0.11388 | 0.13205 | 0.14015 | 0.13387 | 0.21502 | 0.17188 | 0.17601 | 0.18019 | 0.13111 | 0.095463 | 0.095463 | -0.0458 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | CHAP1-_CHAP3-_1 | CHAP1-_CHAP3-_1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00019476 | -0.022951 | -0.030772 | -0.030772 | -0.031106 | -0.030873 | -0.030873 | -0.021271 | 0.02451 | 0.064405 | 0.036195 | 0.1115 | 0.11089 | 0.10037 | 0.072535 | 0.1095 | 0.11388 | 0.13205 | 0.14015 | 0.13387 | 0.21502 | 0.17188 | 0.17601 | 0.18019 | 0.13111 | 0.095463 | 0.095463 | -0.0458 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | CHAP1-_CHAP3-_2 | CHAP1-_CHAP3-_2 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | CHAP1-_M1-_1 | CHAP1-_M1-_1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00019476 | -0.022951 | -0.029156 | -0.029156 | -0.029726 | -0.024491 | -0.024491 | -0.017577 | 0.02518 | 0.067644 | 0.038696 | 0.079756 | 0.079244 | 0.068389 | 0.040914 | 0.069915 | 0.073809 | 0.092036 | 0.099049 | 0.093152 | 0.1746 | 0.13189 | 0.13601 | 0.14019 | 0.091115 | 0.055496 | 0.055496 | -0.058326 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | CHAP1-_M1-_2 | CHAP1-_M1-_2 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00019476 | -0.022951 | -0.029156 | -0.029156 | -0.029726 | -0.024491 | -0.024491 | -0.017577 | 0.02518 | 0.067644 | 0.038696 | 0.079756 | 0.079244 | 0.068389 | 0.040914 | 0.069915 | 0.073809 | 0.092036 | 0.099049 | 0.093152 | 0.1746 | 0.13189 | 0.13601 | 0.14019 | 0.091115 | 0.055496 | 0.055496 | -0.058326 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | CHAP1-_R1-_1 | CHAP1-_R1-_1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | HARK | HARK | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | DUMF-2 | DUMF-2 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | ECCF-2 | ECCF-2 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | GRNA-2 | GRNA-2 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | DUMF-1 | DUMF-1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | ECCF-1 | ECCF-1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | CHAP1-_T1 | CHAP1-_T1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00019476 | -0.022951 | -0.030772 | -0.030772 | -0.031106 | -0.030873 | -0.030873 | -0.021271 | 0.02451 | 0.064405 | 0.036195 | 0.1115 | 0.11089 | 0.10037 | 0.072535 | 0.1095 | 0.11388 | 0.13205 | 0.14015 | 0.13387 | 0.21502 | 0.17188 | 0.17601 | 0.18019 | 0.13111 | 0.095463 | 0.095463 | -0.0458 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | CHAP1-_T2 | CHAP1-_T2 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | GRNA-1 | GRNA-1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016161 | 0.0016161 | 0.0013806 | 0.0063813 | 0.0063813 | 0.0036945 | 0.00066951 | 0.0032387 | 0.0025012 | -0.031741 | -0.031644 | -0.03198 | -0.031621 | -0.039588 | -0.04007 | -0.040018 | -0.041097 | -0.040718 | -0.040424 | -0.039988 | -0.039995 | -0.039995 | -0.039999 | -0.039967 | -0.039967 | -0.012527 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STCR3- | STCR3- | 999 | 0 | 0 | 0 | 0.24101 | 0.46058 | 0.46058 | 0.42106 | 0.42106 | 0.43476 | 0.43568 | 0.45836 | 0.47291 | 0.47291 | 0.47441 | 0.50433 | 0.50433 | 0.45917 | 1.0438 | 1.6923 | 1.9499 | 0.44866 | 1.1973 | 1.7625 | 1.472 | 1.2385 | 1.8362 | 1.2962 | 1.8872 | 1.8967 | 1.8317 | 1.5832 | 1.5837 | 1.5837 | 1.5693 | 1.5721 | 1.5721 | 2.0056 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STCR3-_STCR0G | STCR3-_STCR0G | 999 | 0 | 0 | 0.001 | 0.24101 | 0.46058 | 0.46058 | 0.42106 | 0.42106 | 0.43476 | 0.43568 | 0.45836 | 0.47291 | 0.47291 | 0.47441 | 0.50433 | 0.50433 | 0.45917 | 1.0438 | 1.6923 | 1.9499 | 0.44866 | 1.1973 | 1.7625 | 1.472 | 1.2385 | 1.8362 | 1.2962 | 1.8872 | 1.8967 | 1.8317 | 1.5832 | 1.5837 | 1.5837 | 1.5693 | 1.5721 | 1.5721 | 2.0056 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STCR0G-_2 | STCR0G-_2 | 999 | 0 | 0 | 0.001 | 0.24101 | 0.46058 | 0.46058 | 0.42106 | 0.42106 | 0.43476 | 0.43568 | 0.45836 | 0.47291 | 0.47291 | 0.47441 | 0.50433 | 0.50433 | 0.45917 | 1.0438 | 1.6923 | 1.9499 | 0.44866 | 1.1973 | 1.7625 | 1.472 | 1.2385 | 1.8362 | 1.2962 | 1.8872 | 1.8967 | 1.8317 | 1.5832 | 1.5837 | 1.5837 | 1.5693 | 1.5721 | 1.5721 | 2.0056 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STCR0G-_1 | STCR0G-_1 | 999 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STRC0G-_STCRLVT | STRC0G-_STCRLVT | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STCR_AUX | STCR_AUX | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STCR_DIESEL | STCR_DIESEL | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | minsca33kv | MINS3- | MINS3- | 999 | 0 | 0 | 0 | 0 | 0.001 | 0.034818 | 0.016622 | 0.016622 | 0.020892 | 0.021085 | 0.0099902 | 0.0092886 | 0.0092886 | 0.0090604 | 0.021142 | 0.021142 | 0.011072 | 0.035716 | 0.068459 | 0.061934 | -0.11735 | -0.12388 | -0.1349 | -0.12282 | -0.151 | -0.16515 | -0.27769 | -0.28727 | -0.28357 | -0.28075 | -0.27742 | -0.27748 | -0.27748 | -0.27751 | -0.27722 | -0.27722 | -0.27858 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | minsca33kv | MINS3-_MINSC | MINS3-_MINSC | 999 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.016622 | 0.016622 | 0.020892 | 0.021085 | 0.0099902 | 0.0092886 | 0.0092886 | 0.0090604 | 0.021142 | 0.021142 | 0.011072 | 0.035716 | 0.068459 | 0.061934 | -0.11735 | -0.12388 | -0.1349 | -0.12282 | -0.151 | -0.16515 | -0.27769 | -0.28727 | -0.28357 | -0.28075 | -0.27742 | -0.27748 | -0.27748 | -0.27751 | -0.27722 | -0.27722 | -0.27858 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | minsca33kv | MINS0G | MINS0G | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.016622 | 0.020892 | 0.021085 | 0.0099902 | 0.0092886 | 0.0092886 | 0.0090604 | 0.021142 | 0.021142 | 0.011072 | 0.035716 | 0.068459 | 0.061934 | -0.11735 | -0.12388 | -0.1349 | -0.12282 | -0.151 | -0.16515 | -0.27769 | -0.28727 | -0.28357 | -0.28075 | -0.27742 | -0.27748 | -0.27748 | -0.27751 | -0.27722 | -0.27722 | -0.27858 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ewehillwindfarm1 | EWEH3- | EWEH3- | 999 | 0 | 0 | 0 | 0 | 0.018429 | 0.018429 | 0.01833 | 0.01833 | 0.014983 | 0.015043 | 0.011379 | 0.0096531 | 0.0096531 | 0.0097571 | 0.0085901 | 0.0085901 | 0.011815 | 0.019646 | 0.030379 | 0.059121 | -0.03495 | -0.080564 | -0.08026 | -0.062157 | -0.064382 | -0.077048 | -0.096824 | -0.10515 | -0.10234 | -0.099929 | -0.096508 | -0.096582 | -0.096582 | -0.0926 | -0.092884 | -0.092884 | -0.094255 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ewehillwindfarm1 | EWEH3-_EWEH0G_1 | EWHC3-_EWHC0G_1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01833 | 0.014983 | 0.015043 | 0.011379 | 0.0096531 | 0.0096531 | 0.0097571 | 0.0085901 | 0.0085901 | 0.011815 | 0.019646 | 0.030379 | 0.059121 | -0.03495 | -0.080564 | -0.08026 | -0.062157 | -0.064382 | -0.077048 | -0.096824 | -0.10515 | -0.10234 | -0.099929 | -0.096508 | -0.096582 | -0.096582 | -0.0926 | -0.092884 | -0.092884 | -0.094255 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ewehillwindfarm1 | EWEH0G | EWEH0G | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014983 | 0.015043 | 0.011379 | 0.0096531 | 0.0096531 | 0.0097571 | 0.0085901 | 0.0085901 | 0.011815 | 0.019646 | 0.030379 | 0.059121 | -0.03495 | -0.080564 | -0.08026 | -0.062157 | -0.064382 | -0.077048 | -0.096824 | -0.10515 | -0.10234 | -0.099929 | -0.096508 | -0.096582 | -0.096582 | -0.0926 | -0.092884 | -0.092884 | -0.094255 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | gretna132kv | GRNA1-_SGT1 | GRNA1-_SGT1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013806 | 0.0061735 | 0.0061735 | -0.0054534 | -0.0053381 | 0.0010042 | -0.00047974 | 0.0013811 | 0.00050554 | -1.1767e-05 | 0.00057155 | 0.00063182 | -7.2123e-05 | -2.6156e-05 | -0.00075183 | -0.00054878 | -0.0003623 | 1.567e-06 | -4.9518e-06 | -4.8858e-06 | -8.5183e-06 | 2.2322e-05 | 2.2322e-05 | 0.027566 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | gretna132kv | GRNA1-_SGT2 | GRNA1-_SGT2 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | gretna132kv | GRNA1-_EWEH | GRNA1-_EWEH | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.006772 | 0.006772 | 0.032369 | 0.019755 | 0.010869 | 0.012392 | 0.1352 | 0.12982 | 0.12823 | 0.1301 | 0.16245 | 0.16019 | 0.16026 | 0.16033 | 0.16003 | 0.15996 | 0.1603 | 0.16029 | 0.16029 | 0.16029 | 0.16034 | 0.16034 | 0.18869 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | gretna400kv | GRNA4-_M1-_SGT1 | GRNA4-_M1-_SGT1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013806 | 0.0061735 | 0.0061735 | -0.0054534 | -0.0053381 | 0.0010042 | -0.00047974 | 0.0013811 | 0.00050554 | -1.1767e-05 | 0.00057155 | 0.00063182 | -7.2123e-05 | -2.6156e-05 | -0.00075183 | -0.00054878 | -0.0003623 | 1.567e-06 | -4.9518e-06 | -4.8858e-06 | -8.5183e-06 | 2.2322e-05 | 2.2322e-05 | 0.027566 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcrossgretna1 | CHAP1-_GRNA1 | CHAP1-_GRNA1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016161 | 0.0016161 | 0.0013806 | 0.0063813 | 0.0063813 | 0.0036945 | 0.00066951 | 0.0032387 | 0.0025012 | -0.031741 | -0.031644 | -0.03198 | -0.031621 | -0.039588 | -0.04007 | -0.040018 | -0.041097 | -0.040718 | -0.040424 | -0.039988 | -0.039995 | -0.039995 | -0.039999 | -0.039967 | -0.039967 | -0.012527 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ewehillgretna | EWEH3 | EWEH3 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00059856 | -0.00059856 | -0.037823 | -0.025093 | -0.0098652 | -0.012872 | -0.13382 | -0.12931 | -0.12824 | -0.12953 | -0.16182 | -0.16027 | -0.16029 | -0.16108 | -0.16058 | -0.16032 | -0.1603 | -0.1603 | -0.1603 | -0.1603 | -0.16032 | -0.16032 | -0.16112 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ewehillgretna | EWEH3-_GRID1A-_WG2 | EWEH3-_GRID1A-_WG2 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00059856 | -0.037823 | -0.025093 | -0.0098652 | -0.012872 | -0.13382 | -0.12931 | -0.12824 | -0.12953 | -0.16182 | -0.16027 | -0.16029 | -0.16108 | -0.16058 | -0.16032 | -0.1603 | -0.1603 | -0.1603 | -0.1603 | -0.16032 | -0.16032 | -0.16112 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ewehillwindfarm2 | EWEH0G_2 | EWEH0G_2 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0819e-10 | 0 | 0 | -0.037823 | -0.025093 | -0.0098652 | -0.012872 | -0.13382 | -0.12931 | -0.12824 | -0.12953 | -0.16182 | -0.16027 | -0.16029 | -0.16108 | -0.16058 | -0.16032 | -0.1603 | -0.1603 | -0.1603 | -0.1603 | -0.16032 | -0.16032 | -0.16112 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | gretna400kv | HARK4 | HARK4 | 3.1899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 0.027566 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | gretna400kv | GRNA4-_M1 | GRNA4-_M1 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2322e-05 | 2.2322e-05 | 0.027566 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
End of sheet
Lines are on SLD
Not used in simulation
Vlookup
Copy and paste from PF
[5 empty] | lne_CHAP1-_HAKB1-_1 | A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | #N/A | lne_GRNA1-_JUNV1-_1 | B | -6.9391e-15 | -6.9391e-15 | -6.9388e-15 | -6.9388e-15 | -6.9388e-15 | -6.9388e-15 | -6.9388e-15 | -6.9388e-15 | -6.9388e-15 | -6.9388e-15 | -6.9388e-15 | -6.9388e-15 | -6.9388e-15 | -6.9388e-15 | -6.9393e-15 | -6.9393e-15 | -6.9388e-15 | -6.9388e-15 | -6.9388e-15 | -6.9388e-15 | -6.9388e-15 | -6.9378e-15 | -6.9419e-15 | -6.94e-15 | -6.94e-15 | -6.9372e-15 | -6.942e-15 | -6.9393e-15 | -6.9372e-15 | -6.939e-15 | -6.9386e-15 | -6.938e-15 | -6.938e-15 | -6.9388e-15 | -6.9388e-15 | -6.9386e-15 | -6.9378e-15
[5 empty] | lne_CHAP1-_DUMF1-_1 | C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | MIBI3-_LAHO3A_1 | MIBI3-_LAHO3A_1 | D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27248 | 0.18943 | 0.1189 | 0.1188 | 0.11951 | 0.11928 | 0.12 | 0.11977 | 0.11956 | 0.11925 | 0.11925 | 0.11925 | 0.06771 | 0.074657 | 0.074657 | 0.074752
|  |  |  | CHAPX4_LOBI3A_1 | CHAPX4_LOBI3A_1 | E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1386 | 0.10069 | 0.065307 | 0.064704 | 0.060368 | 0.06037 | 0.060348 | 0.060348 | 0.060426
|  |  |  | CHAP3-_GRNA3B_1 | CHAP3-_GRNA3B_1 | F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26135 | 0.19151 | 0.1914 | 0.1268 | 0.12674 | 0.12766 | 0.12737 | 0.1271 | 0.1267 | 0.12671 | 0.12671 | 0.12671 | 0.084844 | 0.084844 | 0.084977
|  |  |  | CHAPX4_KIBAT1_1 | CHAPX4_KIBAT1_1 | G | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053854 | 0.039375 | 0.025791 | 0.025566 | 0.025592 | 0.025593 | 0.025584 | 0.025584 | 0.025623
|  |  |  | CHAPX4_MOFTT1_1 | CHAPX4_MOFTT1_1 | H | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085202 | 0.061689 | 0.039856 | 0.039481 | 0.035881 | 0.035882 | 0.03587 | 0.03587 | 0.035914
[5 empty] | LAHO3A_LAHOT1_1 | I | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27248 | 0.18943 | 0.1189 | 0.1188 | 0.11951 | 0.11928 | 0.12 | 0.11977 | 0.11956 | 0.11925 | 0.11925 | 0.11925 | 0.06771 | 0.074657 | 0.074657 | 0.074752
|  |  |  | MIBI3-_MIBIT1_1 | MIBI3-_MIBIT1_1 | J | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18236 | 0.089971 | 0.092782 | 0.092162 | 0.091187 | 0.091122 | 0.091616 | 0.091466 | 0.091933 | 0.091784 | 0.09165 | 0.091446 | 0.091451 | 0.091451 | 0.091185 | 0.091206 | 0.091206 | 0.0913
[5 empty] | LAHO3B_LAHOT2_1 | K | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8635e-10 | 3.8656e-10 | 3.8982e-10 | 3.8511e-10 | 3.885e-10 | 3.8937e-10 | 3.8524e-10 | 3.8642e-10 | 3.864e-10 | 3.864e-10 | 0.04916 | 0.042811 | 0.042811 | 0.042936
|  |  |  | CHAPX3_LAHO3B_1 | CHAPX3_LAHO3B_1 | L | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038324 | 0.038304 | 0.028772 | 0.028758 | 0.019206 | 0.019163 | 0.019124 | 0.019065 | 0.019067 | 0.019067 | 0.06823 | 0.061906 | 0.061906 | 0.062049
|  |  |  | LAHO3B_NEWCT1_1 | LAHO3B_NEWCT1_1 | M | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038356 | 0.038336 | 0.028792 | 0.028777 | 0.019208 | 0.019165 | 0.019126 | 0.019067 | 0.019068 | 0.019068 | 0.019255 | 0.019336 | 0.019336 | 0.019364
|  |  |  | LOBI3A_LOBIT1_1 | LOBI3A_LOBIT1_1 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27713 | 0.27696 | 0.20358 | 0.13627 | 0.13464 | 0.13308 | 0.12811 | 0.13055 | 0.13055 | 0.1305 | 0.1305 | 0.13073
|  |  |  | LOBI3B_MOFTT2_1 | LOBI3B_MOFTT2_1 | O | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08344 | 0.039856 | 0.040232 | 0.045494 | 0.045496 | 0.04548 | 0.04548 | 0.045591
|  |  |  | GRNA3B_GRNAT2_1 | GRNA3B_GRNAT2_1 | P | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26145 | 0.19157 | 0.19146 | 0.12681 | 0.12675 | 0.12767 | 0.12738 | 0.12711 | 0.12671 | 0.12672 | 0.12672 | 0.12673 | 0.084868 | 0.084868 | 0.085002
|  |  |  | LOBI3B_LOBIT2_1 | LOBI3B_LOBIT2_1 | Q | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28121 | 0.20399 | 0.13473 | 0.13288 | 0.14289 | 0.14109 | 0.1411 | 0.14105 | 0.14105 | 0.14123
|  |  |  | CHAP3-_MIBI3-_1 | CHAP3-_MIBI3-_1 | R | 0 | 0 | 0 | 0 | 0.018429 | 0.018429 | 0.01833 | 0.01833 | 0.014983 | 0.015043 | 0.011379 | 0.0096531 | 0.0096531 | 0.0097571 | 0.0085901 | 0.0085901 | 0.011815 | 0.019646 | 0.030379 | 0.19936 | 0.059619 | 0.32127 | 0.24715 | 0.1798 | 0.16846 | 0.17334 | 0.12847 | 0.1337 | 0.13187 | 0.13036 | 0.12829 | 0.12833 | 0.12833 | 0.074625 | 0.08143 | 0.08143 | 0.082318
[5 empty] | CHAP3-_CHAPX1_1 | S | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27713 | 0.27696 | 0.20358 | 0.27469 | 0.23503 | 0.19794 | 0.19317 | 0.19076 | 0.19076 | 0.19069 | 0.19069 | 0.19099
|  |  |  | CHAP3-_CHAPX3_1 | CHAP3-_CHAPX3_1 | T | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038404 | 0.038384 | 0.02896 | 0.028946 | 0.019577 | 0.019534 | 0.019498 | 0.019444 | 0.019445 | 0.019445 | 0.068757 | 0.10415 | 0.10415 | 0.10434
|  |  |  | EWEH3-_MIBI3-_1 | EWHC3-_MIBI3-_1 | U | 0 | 0 | 0 | 0 | 0.018429 | 0.018429 | 0.01833 | 0.01833 | 0.014983 | 0.015043 | 0.011379 | 0.0096531 | 0.0096531 | 0.0097571 | 0.0085901 | 0.0085901 | 0.011815 | 0.019646 | 0.030379 | 0.059121 | -0.03495 | -0.080564 | -0.08026 | -0.062157 | -0.064382 | -0.077048 | -0.096824 | -0.10515 | -0.10234 | -0.099929 | -0.096508 | -0.096582 | -0.096582 | -0.0926 | -0.092884 | -0.092884 | -0.094255
|  |  |  | CHAP3-_LOBI3B_1 | CHAP3-_LOBI3B_1 | V | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28095 | 0.20379 | 0.21791 | 0.17212 | 0.18086 | 0.18218 | 0.18219 | 0.18213 | 0.18213 | 0.18238
|  |  |  | GRNA3A_GRNAT1_1 | GRNA3A_GRNAT1_1 | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00012878 | 0.00012885 | 0.00012819 | 0.00012825 | 0.00013077 | 0.00012793 | 0.00012818 | 0.00012858 | 0.00012857 | 0.00012857 | 0.0001308 | 0.041793 | 0.041793 | 0.041839
|  |  |  | ANANT1_CHAP3-_1 | ANANT1_CHAP3-_1 | X | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21054 | 0.21171 | 0.15783 | 0.10427 | 0.10504 | 0.1055 | 0.10499 | 0.10493 | 0.10571 | 0.10566 | 0.1064 | 0.10616 | 0.10595 | 0.10614 | 0.10615 | 0.10615 | 0.10615 | 0.10612 | 0.10612 | 0.10627
|  |  |  | ANANT2_CHAP3-_1 | ANANT2_CHAP3-_1 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21174 | 0.15784 | 0.10427 | 0.10505 | 0.1055 | 0.10499 | 0.10493 | 0.10571 | 0.10566 | 0.1064 | 0.10617 | 0.10595 | 0.10512 | 0.10512 | 0.10512 | 0.10513 | 0.10509 | 0.10509 | 0.10524
|  |  |  | CHAPX1_LOBI3A_1 | CHAPX1_LOBI3A_1 | Z | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27713 | 0.27696 | 0.20358 | 0.27469 | 0.23503 | 0.19794 | 0.19317 | 0.19076 | 0.19076 | 0.19069 | 0.19069 | 0.19099
[5 empty] | CRAG5A_LAHO5-_1 | AA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0931e-09 | -1.1632e-09 | -1.1567e-09 | -1.1576e-09 | -1.1659e-09 | -1.1681e-09 | -1.1611e-09 | -1.1633e-09 | -1.1651e-09 | -1.1682e-09 | -1.1683e-09 | -1.1683e-09 | -1.1678e-09 | -1.163e-09 | -1.163e-09 | -1.1613e-09
[5 empty] | CRAG5B_LAHO5-_1 | AB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.082e-09 | 1.1529e-09 | 1.1461e-09 | 1.1471e-09 | 1.1553e-09 | 1.1576e-09 | 1.1505e-09 | 1.1528e-09 | 1.1548e-09 | 1.1579e-09 | 1.1578e-09 | 1.1578e-09 | 1.1572e-09 | 1.1523e-09 | 1.1523e-09 | 1.1508e-09
|  |  |  | CHAP3-_STCR3-_1 | CHAP3-_STCR3-_1 | AC | 0 | 0 | 0 | 0 | -0.053247 | -0.053247 | -0.033691 | -0.033691 | -0.035721 | -0.035933 | -0.04432 | -0.049714 | -0.049714 | -0.049924 | -0.060604 | -0.060604 | -0.044158 | -0.24139 | -0.45788 | -0.54077 | -0.039308 | -0.2966 | -0.48423 | -0.38593 | -0.30922 | -0.50968 | -0.33376 | -0.53127 | -0.53261 | -0.50998 | -0.42686 | -0.42709 | -0.42707 | -0.42244 | -0.4231 | -0.4231 | -0.56499
|  |  |  | CHAP3-_MINS3-_1 | CHAP3-_MINS3-_1 | AD | 0 | 0 | 0 | 0 | 0.034818 | 0.034818 | 0.016622 | 0.016622 | 0.020892 | 0.021085 | 0.0099902 | 0.0092886 | 0.0092886 | 0.0090604 | 0.021142 | 0.021142 | 0.011072 | 0.035716 | 0.068459 | 0.061934 | -0.11735 | -0.12388 | -0.1349 | -0.12282 | -0.151 | -0.16515 | -0.27769 | -0.28727 | -0.28357 | -0.28075 | -0.27742 | -0.27748 | -0.27748 | -0.27751 | -0.27722 | -0.27722 | -0.27858
|  |  |  | CHAP1-_GRNA1 | lne_AL048A_GRNA1-_1 | AE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016161 | 0.0016161 | 0.0013806 | 0.0063813 | 0.0063813 | 0.0036945 | 0.00066951 | 0.0032387 | 0.0025012 | -0.031741 | -0.031644 | -0.03198 | -0.031621 | -0.039588 | -0.04007 | -0.040018 | -0.041097 | -0.040718 | -0.040424 | -0.039988 | -0.039995 | -0.039995 | -0.039999 | -0.039967 | -0.039967 | -0.012527
|  |  |  | CHAP1-_GRNA1 | lne_CHAP1-_AL048A_1 | AF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044455 | 0.0044455 | 0.0041921 | 0.0095675 | 0.0095675 | 0.00094379 | 0.0022964 | 0.0060281 | 0.0052871 | -0.03151 | -0.031874 | -0.032469 | -0.031818 | -0.039679 | -0.040517 | -0.040442 | -0.041833 | -0.041359 | -0.040975 | -0.040398 | -0.040409 | -0.040408 | -0.040414 | -0.040366 | -0.040366 | -0.015072
|  |  |  | #N/A | lne_EWEH1S_EWEH1R_1 | AG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0002078 | 0.0002078 | 0.0091479 | 0.0060076 | 0.0022345 | 0.002981 | -0.033123 | -0.032149 | -0.031968 | -0.032193 | -0.04022 | -0.039998 | -0.039992 | -0.040345 | -0.04017 | -0.040062 | -0.03999 | -0.03999 | -0.03999 | -0.039991 | -0.039989 | -0.039989 | -0.040092
Manual/Calculated
|  |  |  | chapelcross33kv | CHAP08_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross33kv | CHAP3-_SOLWAY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | CHAP3A1 | Busbar =AC+X+Z+R+F+O+V+Y+AD | 0 | 0 | 0 | 0 | 1.2491e-08 | 1.2491e-08 | 0.001261 | 0.001261 | 0.00015406 | 0.00019476 | -0.022951 | -0.030772 | -0.030772 | -0.031106 | -0.030873 | -0.030873 | -0.021271 | 0.02451 | 0.064405 | 0.036195 | 0.1115 | 0.11089 | 0.10037 | 0.072535 | 0.1095 | 0.11388 | 0.13205 | 0.14015 | 0.13387 | 0.21502 | 0.17188 | 0.17601 | 0.18019 | 0.13111 | 0.095463 | 0.095463 | -0.0458
|  |  |  | chapelcross132kv | CHAP3A2 | Busbar =AC+X+Z+R+F+O+V+Y+AD | 0 | 0 | 0 | 0 | 1.2491e-08 | 1.2491e-08 | 0.001261 | 0.001261 | 0.00015406 | 0.00019476 | -0.022951 | -0.030772 | -0.030772 | -0.031106 | -0.030873 | -0.030873 | -0.021271 | 0.02451 | 0.064405 | 0.036195 | 0.1115 | 0.11089 | 0.10037 | 0.072535 | 0.1095 | 0.11388 | 0.13205 | 0.14015 | 0.13387 | 0.21502 | 0.17188 | 0.17601 | 0.18019 | 0.13111 | 0.095463 | 0.095463 | -0.0458
|  |  |  | chapelcross132kv | CHAP1-_CHAP3-_1 | GRID1 = CHAP3A1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00019476 | -0.022951 | -0.030772 | -0.030772 | -0.031106 | -0.030873 | -0.030873 | -0.021271 | 0.02451 | 0.064405 | 0.036195 | 0.1115 | 0.11089 | 0.10037 | 0.072535 | 0.1095 | 0.11388 | 0.13205 | 0.14015 | 0.13387 | 0.21502 | 0.17188 | 0.17601 | 0.18019 | 0.13111 | 0.095463 | 0.095463 | -0.0458
|  |  |  | chapelcross132kv | CHAP1-_CHAP3-_2 | GRID2 = 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | CHAP1-_M1-_1 | GRNA1+CHAP-T1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00019476 | -0.022951 | -0.029156 | -0.029156 | -0.029726 | -0.024491 | -0.024491 | -0.017577 | 0.02518 | 0.067644 | 0.038696 | 0.079756 | 0.079244 | 0.068389 | 0.040914 | 0.069915 | 0.073809 | 0.092036 | 0.099049 | 0.093152 | 0.1746 | 0.13189 | 0.13601 | 0.14019 | 0.091115 | 0.055496 | 0.055496 | -0.058326
|  |  |  | chapelcross132kv | CHAP1-_M1-_2 | GRNA1+CHAP-T1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00019476 | -0.022951 | -0.029156 | -0.029156 | -0.029726 | -0.024491 | -0.024491 | -0.017577 | 0.02518 | 0.067644 | 0.038696 | 0.079756 | 0.079244 | 0.068389 | 0.040914 | 0.069915 | 0.073809 | 0.092036 | 0.099049 | 0.093152 | 0.1746 | 0.13189 | 0.13601 | 0.14019 | 0.091115 | 0.055496 | 0.055496 | -0.058326
|  |  |  | chapelcross132kv | CHAP1-_R1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | HARK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | DUMF-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | ECCF-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | GRNA-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | DUMF-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | ECCF-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | CHAP1-_T1 | GRID1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00019476 | -0.022951 | -0.030772 | -0.030772 | -0.031106 | -0.030873 | -0.030873 | -0.021271 | 0.02451 | 0.064405 | 0.036195 | 0.1115 | 0.11089 | 0.10037 | 0.072535 | 0.1095 | 0.11388 | 0.13205 | 0.14015 | 0.13387 | 0.21502 | 0.17188 | 0.17601 | 0.18019 | 0.13111 | 0.095463 | 0.095463 | -0.0458
|  |  |  | chapelcross132kv | CHAP1-_T2 | GRID2=0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | GRNA-1 | AE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016161 | 0.0016161 | 0.0013806 | 0.0063813 | 0.0063813 | 0.0036945 | 0.00066951 | 0.0032387 | 0.0025012 | -0.031741 | -0.031644 | -0.03198 | -0.031621 | -0.039588 | -0.04007 | -0.040018 | -0.041097 | -0.040718 | -0.040424 | -0.039988 | -0.039995 | -0.039995 | -0.039999 | -0.039967 | -0.039967 | -0.012527
|  |  |  | stevenscroft33kv | STCR3- | Busbar | 0 | 0 | 0 | 0.24101 | 0.46058 | 0.46058 | 0.42106 | 0.42106 | 0.43476 | 0.43568 | 0.45836 | 0.47291 | 0.47291 | 0.47441 | 0.50433 | 0.50433 | 0.45917 | 1.0438 | 1.6923 | 1.9499 | 0.44866 | 1.1973 | 1.7625 | 1.472 | 1.2385 | 1.8362 | 1.2962 | 1.8872 | 1.8967 | 1.8317 | 1.5832 | 1.5837 | 1.5837 | 1.5693 | 1.5721 | 1.5721 | 2.0056
|  |  |  | stevenscroft33kv | STCR3-_STCR0G | Calc from Trfr STCR3-_STCR5-_1 | 0 | 0 | 0.001 | 0.24101 | 0.46058 | 0.46058 | 0.42106 | 0.42106 | 0.43476 | 0.43568 | 0.45836 | 0.47291 | 0.47291 | 0.47441 | 0.50433 | 0.50433 | 0.45917 | 1.0438 | 1.6923 | 1.9499 | 0.44866 | 1.1973 | 1.7625 | 1.472 | 1.2385 | 1.8362 | 1.2962 | 1.8872 | 1.8967 | 1.8317 | 1.5832 | 1.5837 | 1.5837 | 1.5693 | 1.5721 | 1.5721 | 2.0056
|  |  |  | stevenscroft33kv | STCR0G-_2 | Calc from Trfr STCR3-_STCR5-_1 | 0 | 0 | 0.001 | 0.24101 | 0.46058 | 0.46058 | 0.42106 | 0.42106 | 0.43476 | 0.43568 | 0.45836 | 0.47291 | 0.47291 | 0.47441 | 0.50433 | 0.50433 | 0.45917 | 1.0438 | 1.6923 | 1.9499 | 0.44866 | 1.1973 | 1.7625 | 1.472 | 1.2385 | 1.8362 | 1.2962 | 1.8872 | 1.8967 | 1.8317 | 1.5832 | 1.5837 | 1.5837 | 1.5693 | 1.5721 | 1.5721 | 2.0056
|  |  |  | stevenscroft33kv | STCR0G-_1 | Busbar | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | stevenscroft33kv | STRC0G-_STCRLVT | Busbar | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | stevenscroft33kv | STCR_AUX | Busbar | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | stevenscroft33kv | STCR_DIESEL | Busbar | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | minsca33kv | MINS3- | AD | 0 | 0 | 0 | 0 | 0.001 | 0.034818 | 0.016622 | 0.016622 | 0.020892 | 0.021085 | 0.0099902 | 0.0092886 | 0.0092886 | 0.0090604 | 0.021142 | 0.021142 | 0.011072 | 0.035716 | 0.068459 | 0.061934 | -0.11735 | -0.12388 | -0.1349 | -0.12282 | -0.151 | -0.16515 | -0.27769 | -0.28727 | -0.28357 | -0.28075 | -0.27742 | -0.27748 | -0.27748 | -0.27751 | -0.27722 | -0.27722 | -0.27858
|  |  |  | minsca33kv | MINS3-_MINSC | AD | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.016622 | 0.016622 | 0.020892 | 0.021085 | 0.0099902 | 0.0092886 | 0.0092886 | 0.0090604 | 0.021142 | 0.021142 | 0.011072 | 0.035716 | 0.068459 | 0.061934 | -0.11735 | -0.12388 | -0.1349 | -0.12282 | -0.151 | -0.16515 | -0.27769 | -0.28727 | -0.28357 | -0.28075 | -0.27742 | -0.27748 | -0.27748 | -0.27751 | -0.27722 | -0.27722 | -0.27858
|  |  |  | minsca33kv | MINS0G | AD | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.016622 | 0.020892 | 0.021085 | 0.0099902 | 0.0092886 | 0.0092886 | 0.0090604 | 0.021142 | 0.021142 | 0.011072 | 0.035716 | 0.068459 | 0.061934 | -0.11735 | -0.12388 | -0.1349 | -0.12282 | -0.151 | -0.16515 | -0.27769 | -0.28727 | -0.28357 | -0.28075 | -0.27742 | -0.27748 | -0.27748 | -0.27751 | -0.27722 | -0.27722 | -0.27858
|  |  |  | ewehillwindfarm1 | EWEH3- | U | 0 | 0 | 0 | 0 | 0.018429 | 0.018429 | 0.01833 | 0.01833 | 0.014983 | 0.015043 | 0.011379 | 0.0096531 | 0.0096531 | 0.0097571 | 0.0085901 | 0.0085901 | 0.011815 | 0.019646 | 0.030379 | 0.059121 | -0.03495 | -0.080564 | -0.08026 | -0.062157 | -0.064382 | -0.077048 | -0.096824 | -0.10515 | -0.10234 | -0.099929 | -0.096508 | -0.096582 | -0.096582 | -0.0926 | -0.092884 | -0.092884 | -0.094255
|  |  |  | ewehillwindfarm1 | EWHC3-_EWHC0G_1 | U | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01833 | 0.014983 | 0.015043 | 0.011379 | 0.0096531 | 0.0096531 | 0.0097571 | 0.0085901 | 0.0085901 | 0.011815 | 0.019646 | 0.030379 | 0.059121 | -0.03495 | -0.080564 | -0.08026 | -0.062157 | -0.064382 | -0.077048 | -0.096824 | -0.10515 | -0.10234 | -0.099929 | -0.096508 | -0.096582 | -0.096582 | -0.0926 | -0.092884 | -0.092884 | -0.094255
|  |  |  | ewehillwindfarm1 | EWEH0G | U | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014983 | 0.015043 | 0.011379 | 0.0096531 | 0.0096531 | 0.0097571 | 0.0085901 | 0.0085901 | 0.011815 | 0.019646 | 0.030379 | 0.059121 | -0.03495 | -0.080564 | -0.08026 | -0.062157 | -0.064382 | -0.077048 | -0.096824 | -0.10515 | -0.10234 | -0.099929 | -0.096508 | -0.096582 | -0.096582 | -0.0926 | -0.092884 | -0.092884 | -0.094255
|  |  |  | gretna132kv | GRNA1-_SGT1 | AE-AG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013806 | 0.0061735 | 0.0061735 | -0.0054534 | -0.0053381 | 0.0010042 | -0.00047974 | 0.0013811 | 0.00050554 | -1.1767e-05 | 0.00057155 | 0.00063182 | -7.2123e-05 | -2.6156e-05 | -0.00075183 | -0.00054878 | -0.0003623 | 1.567e-06 | -4.9518e-06 | -4.8858e-06 | -8.5183e-06 | 2.2322e-05 | 2.2322e-05 | 0.027566
|  |  |  | gretna132kv | GRNA1-_SGT2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | gretna132kv | GRNA1-_EWEH | =-GT1+AE-AG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.006772 | 0.006772 | 0.032369 | 0.019755 | 0.010869 | 0.012392 | 0.1352 | 0.12982 | 0.12823 | 0.1301 | 0.16245 | 0.16019 | 0.16026 | 0.16033 | 0.16003 | 0.15996 | 0.1603 | 0.16029 | 0.16029 | 0.16029 | 0.16034 | 0.16034 | 0.18869
|  |  |  | gretna400kv | GRNA4-_M1-_SGT1 | GRNA-_SGT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013806 | 0.0061735 | 0.0061735 | -0.0054534 | -0.0053381 | 0.0010042 | -0.00047974 | 0.0013811 | 0.00050554 | -1.1767e-05 | 0.00057155 | 0.00063182 | -7.2123e-05 | -2.6156e-05 | -0.00075183 | -0.00054878 | -0.0003623 | 1.567e-06 | -4.9518e-06 | -4.8858e-06 | -8.5183e-06 | 2.2322e-05 | 2.2322e-05 | 0.027566
|  |  |  | chapelcrossgretna1 | CHAP1-_GRNA1 | AE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016161 | 0.0016161 | 0.0013806 | 0.0063813 | 0.0063813 | 0.0036945 | 0.00066951 | 0.0032387 | 0.0025012 | -0.031741 | -0.031644 | -0.03198 | -0.031621 | -0.039588 | -0.04007 | -0.040018 | -0.041097 | -0.040718 | -0.040424 | -0.039988 | -0.039995 | -0.039995 | -0.039999 | -0.039967 | -0.039967 | -0.012527
|  |  |  | ewehillgretna | EWEH3 | GT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00059856 | -0.00059856 | -0.037823 | -0.025093 | -0.0098652 | -0.012872 | -0.13382 | -0.12931 | -0.12824 | -0.12953 | -0.16182 | -0.16027 | -0.16029 | -0.16108 | -0.16058 | -0.16032 | -0.1603 | -0.1603 | -0.1603 | -0.1603 | -0.16032 | -0.16032 | -0.16112
|  |  |  | ewehillgretna | EWEH3-_GRID1A-_WG2 | GT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00059856 | -0.037823 | -0.025093 | -0.0098652 | -0.012872 | -0.13382 | -0.12931 | -0.12824 | -0.12953 | -0.16182 | -0.16027 | -0.16029 | -0.16108 | -0.16058 | -0.16032 | -0.1603 | -0.1603 | -0.1603 | -0.1603 | -0.16032 | -0.16032 | -0.16112
|  |  |  | ewehillwindfarm2 | EWEH0G_2 | GT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0819e-10 | 0 | 0 | -0.037823 | -0.025093 | -0.0098652 | -0.012872 | -0.13382 | -0.12931 | -0.12824 | -0.12953 | -0.16182 | -0.16027 | -0.16029 | -0.16108 | -0.16058 | -0.16032 | -0.1603 | -0.1603 | -0.1603 | -0.1603 | -0.16032 | -0.16032 | -0.16112
|  |  |  | gretna400kv | HARK4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 0.027566
|  |  |  | gretna400kv | GRNA4-_M1 | SGT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2322e-05 | 2.2322e-05 | 0.027566

## Lines - Active Power
Lines - Active Power
Results
Lines
[6 empty] | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[6 empty] | Active Power >>> | [36 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  | network | Name | PF Name | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  | chapelcross33kv |  | lne_CHAP1-_HAKB1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | chapelcross33kv |  | CRAG5B_LAHO5-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9516e-08 | 2.2128e-08 | 2.1873e-08 | 2.191e-08 | 2.2221e-08 | 2.2308e-08 | 2.2039e-08 | 2.2124e-08 | 2.2202e-08 | 2.232e-08 | 2.2317e-08 | 2.2317e-08 | 2.2293e-08 | 2.2108e-08 | 2.2108e-08 | 2.205e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7212e-08 | 2.118e-08 | 2.2107e-08 | 2.1958e-08 | 2.2058e-08 | 2.1967e-08 | 2.1947e-08
|  |  | chapelcross33kv | CHAPX3_LAHO3B_1 | CHAPX3_LAHO3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2027 | 2.2027 | 1.6478 | 1.6478 | 1.0957 | 1.0957 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 3.8672 | 3.4861 | 3.4861 | 3.4882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.203 | 1.0958 | 1.0957 | 1.0957 | 3.519
|  |  | chapelcross33kv | LOBI3B_MOFTT2_1 | LOBI3B_MOFTT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5797 | 2.2075 | 2.2088 | 2.4524 | 2.4524 | 2.4523 | 2.4523 | 2.4537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5842 | 2.4534
|  |  | chapelcross33kv |  | lne_CHAP1-_DUMF1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | chapelcross33kv | CHAP3-_LOBI3B_1 | CHAP3-_LOBI3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5839 | 11.4873 | 12.4235 | 9.8719 | 10.1479 | 10.2766 | 10.2766 | 10.2765 | 10.2765 | 10.2772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6102 | 7.5441 | 12.4343 | 10.2782
|  |  | chapelcross33kv |  | CHAP3-_CHAPX1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5499 | 15.5488 | 11.4755 | 15.6293 | 13.4363 | 11.3685 | 11.1061 | 10.9767 | 10.9768 | 10.9763 | 10.9763 | 10.9782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5853 | 15.634 | 13.4472 | 10.9826
|  |  | chapelcross33kv | CHAPX4_KIBAT1_1 | CHAPX4_KIBAT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7692 | 2.0672 | 1.3724 | 1.3722 | 1.3722 | 1.3722 | 1.3722 | 1.3722 | 1.3722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7693 | 2.0676 | 1.3723
|  |  | chapelcross33kv | CHAPX4_MOFTT1_1 | CHAPX4_MOFTT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4048 | 3.2754 | 2.1672 | 2.1666 | 1.9367 | 1.9367 | 1.9367 | 1.9367 | 1.9355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4053 | 3.2764 | 1.9365
|  |  | chapelcross33kv | CHAP3-_CHAPX3_1 | CHAP3-_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2101 | 2.2101 | 1.6552 | 1.6552 | 1.1032 | 1.103 | 1.103 | 1.103 | 1.103 | 1.103 | 3.8747 | 5.8371 | 5.8371 | 5.8386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2105 | -1.1031 | -1.1032 | -1.1032 | -5.8634
|  |  | chapelcross33kv | GRNA3A_GRNAT1_1 | GRNA3A_GRNAT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007417 | 0.0074247 | 0.0073487 | 0.0073559 | 0.0074648 | 0.0073185 | 0.007348 | 0.0073929 | 0.0073919 | 0.0073919 | 0.0074677 | 2.3375 | 2.3375 | 2.3369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0074753 | 0.0072647 | 0.0074765 | 0.0074412 | 2.331
|  |  | chapelcross33kv | LOBI3A_LOBIT1_1 | LOBI3A_LOBIT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.7613 | 14.7612 | 11.05 | 7.3537 | 7.3537 | 7.3538 | 7.1125 | 7.2323 | 7.2323 | 7.2321 | 7.2321 | 7.2338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.7603 | 7.3537 | 7.3534 | 7.2346
|  |  | chapelcross33kv |  | LAHO3A_LAHOT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.7756 | 9.5589 | 6.3643 | 6.3643 | 6.3641 | 6.364 | 6.3642 | 6.3641 | 6.3641 | 6.364 | 6.364 | 6.364 | 3.601 | 3.979 | 3.979 | 3.977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.7881 | 9.5608 | 6.3641 | 6.3642 | 6.3642 | 6.3642 | 3.9467
|  |  | chapelcross33kv |  | LAHO3B_LAHOT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2167e-08 | 2.219e-08 | 2.2282e-08 | 2.2024e-08 | 2.2131e-08 | 2.223e-08 | 2.2039e-08 | 2.2174e-08 | 2.2171e-08 | 2.2171e-08 | 2.7525 | 2.3751 | 2.3751 | 2.3771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2081e-08 | 2.1817e-08 | 2.2166e-08 | 2.2061e-08 | 2.4074
|  |  | chapelcross33kv | MIBI3-_MIBIT1_1 | MIBI3-_MIBIT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4903 | 5.2316 | 5.2317 | 5.2319 | 5.2316 | 5.2316 | 5.2317 | 5.2317 | 5.2318 | 5.2318 | 5.2317 | 5.2317 | 5.2317 | 5.2317 | 5.2316 | 5.2316 | 5.2316 | 5.2316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4908 | 7.8586 | 5.2319 | 5.2317 | 5.2318 | 5.2318 | 5.2318 | 5.2317
|  |  | chapelcross33kv | GRNA3B_GRNAT2_1 | GRNA3B_GRNAT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.3947 | 10.7766 | 10.7765 | 7.1722 | 7.1722 | 7.1725 | 7.1724 | 7.1723 | 7.1722 | 7.1722 | 7.1722 | 7.1722 | 4.8297 | 4.8297 | 4.8303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.395 | 10.7762 | 7.1726 | 7.1725 | 7.1726 | 4.8362
|  |  | chapelcross33kv | MIBI3-_LAHO3A_1 | MIBI3-_LAHO3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.7706 | 10.5232 | 6.7442 | 6.7435 | 6.7479 | 6.7463 | 6.7511 | 6.7496 | 6.7482 | 6.7461 | 6.7462 | 6.7462 | 3.7242 | 4.1288 | 4.1288 | 4.1272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.0469 | 10.5959 | 6.7601 | 6.7629 | 6.7508 | 6.7524 | 4.0957
|  |  | chapelcross33kv | LAHO3B_NEWCT1_1 | LAHO3B_NEWCT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1962 | 2.1961 | 1.6441 | 1.6441 | 1.0941 | 1.094 | 1.094 | 1.094 | 1.094 | 1.094 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1963 | 1.0941 | 1.094 | 1.0941 | 1.0941
|  |  | chapelcross33kv | CHAP3-_MIBI3-_1 | CHAP3-_MIBI3-_1 | 0 | 0 | 0 | 0 | 0.0018917 | 0.0018917 | 0.0018714 | 0.0018714 | 0.50146 | 0.50147 | 0.50106 | 0.50104 | 0.50104 | 0.50104 | 0.50146 | 0.50146 | 0.50109 | 0.50243 | 0.5064 | 11.1793 | 3.353 | 18.587 | 14.1527 | 10.2344 | 9.6183 | 9.6379 | 7.1963 | 7.2146 | 7.2083 | 7.203 | 7.1957 | 7.1958 | 7.1958 | 4.1224 | 4.5319 | 4.5319 | 4.532 | 0 | 0 | 0 | 0 | 0.50104 | 0.50103 | 0.50103 | 0.50107 | 11.1676 | 24.256 | 16.7204 | 12.7106 | 7.6421 | 7.6171 | 7.6244 | 4.9044
|  |  | chapelcross33kv | ANANT1_CHAP3-_1 | ANANT1_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2314 | 12.233 | 9.1469 | 6.0812 | 6.0814 | 6.0816 | 6.0813 | 6.0813 | 6.0818 | 6.0817 | 6.0822 | 6.082 | 6.0819 | 6.1113 | 6.1113 | 6.1113 | 6.1113 | 6.1113 | 6.1113 | 6.1114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2382 | 9.1505 | 6.0823 | 6.0825 | 6.0818 | 6.0827 | 6.0821 | 6.0823 | 6.1115
|  |  | chapelcross33kv |  | CARU3A_CHAPX1_1 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0623e-08 | -1.0945e-08 | -1.0907e-08 | -1.1042e-08
|  |  | chapelcross33kv | ANANT2_CHAP3-_1 | ANANT2_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2334 | 9.1471 | 6.0813 | 6.0815 | 6.0817 | 6.0814 | 6.0814 | 6.0819 | 6.0818 | 6.0823 | 6.0821 | 6.082 | 6.0522 | 6.0522 | 6.0522 | 6.0522 | 6.0522 | 6.0522 | 6.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2387 | 9.1508 | 6.0824 | 6.0825 | 6.0819 | 6.0828 | 6.0822 | 6.0824 | 6.0524
|  |  | chapelcross33kv | EWEH3-_MIBI3-_1 | EWHC3-_MIBI3-_1 | 0 | 0 | 0 | 0 | 0.00038577 | 0.00038577 | 0.00038163 | 0.00038165 | 0.50046 | 0.50046 | 0.50049 | 0.50063 | 0.50063 | 0.50062 | 0.50113 | 0.50113 | 0.50047 | 0.50072 | 0.50231 | 0.51275 | -1.8943 | -1.8729 | -1.8732 | -1.8847 | -2.4826 | -2.4749 | -4.8548 | -4.8475 | -4.8501 | -4.8522 | -4.8551 | -4.855 | -4.855 | -4.8581 | -4.8579 | -4.8579 | -4.8569 | 0 | 0 | 0 | 0 | 0.50056 | 0.50056 | 0.50055 | 0.50062 | 0.50066 | 0.50069 | 0.50065 | 0.50062 | -4.4466 | -4.453 | -4.45 | -4.4597
|  |  | chapelcross33kv |  | CRAG5A_LAHO5-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9716e-08 | -2.2326e-08 | -2.2075e-08 | -2.2111e-08 | -2.2425e-08 | -2.251e-08 | -2.2242e-08 | -2.2326e-08 | -2.24e-08 | -2.2519e-08 | -2.2519e-08 | -2.2519e-08 | -2.2498e-08 | -2.2314e-08 | -2.2314e-08 | -2.2251e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7411e-08 | -2.1377e-08 | -2.2306e-08 | -2.2156e-08 | -2.226e-08 | -2.2168e-08 | -2.2145e-08
|  |  | chapelcross33kv | CHAPX4_LOBI3A_1 | CHAPX4_LOBI3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.174 | 5.3426 | 3.5395 | 3.5388 | 3.3089 | 3.3089 | 3.3089 | 3.3089 | 3.3077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.1747 | -5.3439 | -3.3088
|  |  | chapelcross33kv | CHAPX1_LOBI3A_1 | CHAPX1_LOBI3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5012 | 15.5002 | 11.4493 | 15.5815 | 13.4013 | 11.3437 | 11.0824 | 10.9537 | 10.9537 | 10.9532 | 10.9532 | 10.9551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5345 | 15.5861 | 13.4118 | 10.9593
|  |  | chapelcross33kv | CHAP3-_GRNA3B_1 | CHAP3-_GRNA3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9083 | 11.0523 | 11.052 | 7.2931 | 7.2929 | 7.295 | 7.2943 | 7.2937 | 7.2928 | 7.2929 | 7.2929 | 7.2929 | 4.8838 | 4.8838 | 4.8846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9233 | 11.0566 | 7.2985 | 7.2948 | 7.2955 | 4.8909
|  |  | chapelcross33kv | CHAP3-_MINS3-_1 | CHAP3-_MINS3-_1 | 0 | 0 | 0 | 0 | 0.00062978 | 0.00062979 | 0.50026 | 0.50026 | 0.50022 | 0.50022 | 0.50063 | 0.50135 | 0.50135 | 0.50128 | 0.5035 | 0.5035 | 0.50053 | 0.5008 | 0.50572 | 0.50435 | -6.8274 | -6.8277 | -6.8235 | -6.828 | -8.6496 | -8.6433 | -15.8876 | -15.8789 | -15.8825 | -15.8851 | -15.8878 | -15.8877 | -15.8877 | -15.8877 | -15.8879 | -15.8879 | -15.8869 | 0 | 0 | 0 | 0.5024 | 0.50239 | 0.50236 | 0.50232 | 0.5027 | 0.50274 | -19.2368 | -19.2326 | -19.2465 | -19.2055 | -19.242 | -19.2383 | -19.2452
|  |  | chapelcross33kv | CHAP3-_STCR3-_1 | CHAP3-_STCR3-_1 | 0 | 0 | 0 | 0 | -0.0025215 | -0.0025215 | -0.50213 | -0.50213 | -1.0017 | -1.0301 | -1.0306 | -1.0318 | -1.0318 | -1.0928 | -1.1466 | -1.1466 | -1.121 | -13.353 | -25.5963 | -30.0954 | -1.4689 | -16.7015 | -27.18 | -21.6272 | -17.3614 | -28.6171 | -18.9299 | -29.8979 | -29.9436 | -28.6779 | -24.0635 | -24.0772 | -24.0766 | -23.8226 | -23.8514 | -23.8514 | -31.6373 | 0 | -1.1415e-08 | -1.1415e-08 | -0.5024 | -1.0034 | -1.032 | -1.122 | -25.5556 | -30.046 | -17.2609 | -24.6528 | -19.0103 | -40.2792 | -32.2178 | -34.9124 | -30.0579
|  |  | chapelcross33kv | LOBI3B_LOBIT2_1 | LOBI3B_LOBIT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.791 | 11.0701 | 7.3671 | 7.367 | 7.6104 | 7.4907 | 7.4907 | 7.4909 | 7.4909 | 7.4893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.7916 | 7.367 | 7.3668 | 7.4888
|  |  | chapelcross33kv | CHAP1-_GRNA1 | lne_AL048A_GRNA1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3385e-08 | 4.3385e-08 | 0.06113 | 0.11085 | 0.11085 | 0.090476 | 0.089545 | 0.088773 | 0.088896 | -7.2563 | -7.2576 | -7.2581 | -7.2575 | -9.0898 | -9.0905 | -9.0905 | -9.107 | -9.1071 | -9.1071 | -9.0905 | -9.0905 | -9.0905 | -9.0905 | -9.0905 | -9.0905 | -1.2999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | chapelcross33kv | CHAP1-_GRNA1 | lne_CHAP1-_AL048A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0163e-05 | 6.0163e-05 | 0.061181 | 0.11124 | 0.11124 | 0.090513 | 0.089554 | 0.088908 | 0.088992 | -7.2502 | -7.2515 | -7.2517 | -7.2514 | -9.0802 | -9.0806 | -9.0806 | -9.0965 | -9.0968 | -9.097 | -9.0806 | -9.0806 | -9.0806 | -9.0806 | -9.0806 | -9.0806 | -1.2987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | chapelcross33kv |  | lne_AL048B_GRNA1-_1 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | 0 | 0 | 0 | 0 | 4.2666e-08 | 0.089274 | 0.048097 | 0.047718 | 0.049429 | 0.049229 | 0.070616 | 0.048344 | 0.070013 | 0.049508 | 0.070398
|  |  | chapelcross33kv |  | lne_CHAP1-_AL048B_1 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | 0 | 0 | 0 | 0 | 5.9126e-05 | 0.089581 | 0.048286 | 0.047906 | 0.049624 | 0.049423 | 0.070918 | 0.048535 | 0.070312 | 0.049703 | 0.070699
|  |  | chapelcross33kv |  | CHAP08_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4699e-12 | 6.556e-12 | 4.0008e-12 | 3.9671e-12 | 4.1085e-12 | 4.0925e-12 | 6.3278e-12 | 4.0187e-12 | 6.2697e-12 | 4.1164e-12 | 6.2973e-12
|  |  | chapelcross33kv | CHAP3-_SOLWAY | CHAP3-_SOLWAY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3269e-12 | -2.355e-12 | -1.4335e-12 | -1.4222e-12 | -1.4732e-12 | -1.4673e-12 | -2.2689e-12 | -1.4409e-12 | -2.2489e-12 | -1.4756e-12 | -2.2614e-12
|  |  | chapelcross132kv | CHAP3A1 | CHAP3A1 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | chapelcross132kv | CHAP3A2 | CHAP3A2 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | chapelcross132kv | CHAP1-_CHAP3-_1 | CHAP1-_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | chapelcross132kv | CHAP1-_CHAP3-_2 | CHAP1-_CHAP3-_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | chapelcross132kv | CHAP1-_M1-_1 | CHAP1-_M1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | CHAP1-_M1-_2 | CHAP1-_M1-_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | CHAP1-_R1-_1 | CHAP1-_R1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | HARK | HARK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | DUMF-2 | DUMF-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | ECCF-2 | ECCF-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | GRNA-2 | GRNA-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | DUMF-1 | DUMF-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | ECCF-1 | ECCF-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | CHAP1-_T1 | CHAP1-_T1 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | CHAP1-_T2 | CHAP1-_T2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | GRNA-1 | GRNA-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STCR3- | STCR3- | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STCR3-_STCR0G | STCR3-_STCR0G | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STCR0G-_2 | STCR0G-_2 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STCR0G-_1 | STCR0G-_1 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STRC0G-_STCRLVT | STRC0G-_STCRLVT | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STCR_AUX | STCR_AUX | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STCR_DIESEL | STCR_DIESEL | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | minsca33kv | MINS3- | MINS3- | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | minsca33kv | MINS3-_MINSC | MINS3-_MINSC | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | minsca33kv | MINS0G | MINS0G | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ewehillwindfarm1 | EWEH3- | EWEH3- | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ewehillwindfarm1 | EWEH3-_EWEH0G_1 | EWHC3-_EWHC0G_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ewehillwindfarm1 | EWEH0G | EWEH0G | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | gretna132kv | GRNA1-_SGT1 | GRNA1-_SGT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | gretna132kv | GRNA1-_SGT2 | GRNA1-_SGT2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | gretna132kv | GRNA1-_EWEH | GRNA1-_EWEH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | gretna400kv | GRNA4-_M1-_SGT1 | GRNA4-_M1-_SGT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcrossgretna1 | CHAP1-_GRNA1 | CHAP1-_GRNA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ewehillgretna | EWEH3 | EWEH3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ewehillgretna | EWEH3-_GRID1A-_WG2 | EWEH3-_GRID1A-_WG2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ewehillwindfarm2 | EWEH0G_2 | EWEH0G_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | gretna400kv | HARK4 | HARK4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | gretna400kv | GRNA4-_M1 | GRNA4-_M1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
End of sheet
Lines are on SLD
Not used in simulation
Vlookup
Copy and paste from PF
[5 empty] | lne_CHAP1-_HAKB1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | lne_GRNA1-_JUNV1-_1 | -2.2883e-16 | -2.2883e-16 | -2.2882e-16 | -2.2882e-16 | -2.2882e-16 | -2.2882e-16 | -2.2882e-16 | -2.2882e-16 | -2.2882e-16 | -2.2882e-16 | -2.2882e-16 | -2.2882e-16 | -2.2882e-16 | -2.2882e-16 | -2.2884e-16 | -2.2884e-16 | -2.2882e-16 | -2.2882e-16 | -2.2882e-16 | -2.2882e-16 | -2.2882e-16 | -2.2879e-16 | -2.2892e-16 | -2.2886e-16 | -2.2886e-16 | -2.2877e-16 | -2.2893e-16 | -2.2884e-16 | -2.2877e-16 | -2.2883e-16 | -2.2881e-16 | -2.2879e-16 | -2.2879e-16 | -2.2882e-16 | -2.2882e-16 | -2.2881e-16 | -2.2877e-16
[5 empty] | lne_CHAP1-_DUMF1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | MIBI3-_LAHO3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.7706 | 10.5232 | 6.7442 | 6.7435 | 6.7479 | 6.7463 | 6.7511 | 6.7496 | 6.7482 | 6.7461 | 6.7462 | 6.7462 | 3.7242 | 4.1288 | 4.1288 | 4.1272
[5 empty] | CHAPX4_LOBI3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.174 | 5.3426 | 3.5395 | 3.5388 | 3.3089 | 3.3089 | 3.3089 | 3.3089 | 3.3077
[5 empty] | CHAP3-_GRNA3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9083 | 11.0523 | 11.052 | 7.2931 | 7.2929 | 7.295 | 7.2943 | 7.2937 | 7.2928 | 7.2929 | 7.2929 | 7.2929 | 4.8838 | 4.8838 | 4.8846
[5 empty] | CHAPX4_KIBAT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7692 | 2.0672 | 1.3724 | 1.3722 | 1.3722 | 1.3722 | 1.3722 | 1.3722 | 1.3722
[5 empty] | CHAPX4_MOFTT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4048 | 3.2754 | 2.1672 | 2.1666 | 1.9367 | 1.9367 | 1.9367 | 1.9367 | 1.9355
[5 empty] | LAHO3A_LAHOT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.7756 | 9.5589 | 6.3643 | 6.3643 | 6.3641 | 6.364 | 6.3642 | 6.3641 | 6.3641 | 6.364 | 6.364 | 6.364 | 3.601 | 3.979 | 3.979 | 3.977
[5 empty] | MIBI3-_MIBIT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4903 | 5.2316 | 5.2317 | 5.2319 | 5.2316 | 5.2316 | 5.2317 | 5.2317 | 5.2318 | 5.2318 | 5.2317 | 5.2317 | 5.2317 | 5.2317 | 5.2316 | 5.2316 | 5.2316 | 5.2316
[5 empty] | LAHO3B_LAHOT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2167e-08 | 2.219e-08 | 2.2282e-08 | 2.2024e-08 | 2.2131e-08 | 2.223e-08 | 2.2039e-08 | 2.2174e-08 | 2.2171e-08 | 2.2171e-08 | 2.7525 | 2.3751 | 2.3751 | 2.3771
[5 empty] | CHAPX3_LAHO3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2027 | 2.2027 | 1.6478 | 1.6478 | 1.0957 | 1.0957 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 3.8672 | 3.4861 | 3.4861 | 3.4882
[5 empty] | LAHO3B_NEWCT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1962 | 2.1961 | 1.6441 | 1.6441 | 1.0941 | 1.094 | 1.094 | 1.094 | 1.094 | 1.094 | 1.0941 | 1.0941 | 1.0941 | 1.0941
[5 empty] | LOBI3A_LOBIT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.7613 | 14.7612 | 11.05 | 7.3537 | 7.3537 | 7.3538 | 7.1125 | 7.2323 | 7.2323 | 7.2321 | 7.2321 | 7.2338
[5 empty] | LOBI3B_MOFTT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5797 | 2.2075 | 2.2088 | 2.4524 | 2.4524 | 2.4523 | 2.4523 | 2.4537
[5 empty] | GRNA3B_GRNAT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.3947 | 10.7766 | 10.7765 | 7.1722 | 7.1722 | 7.1725 | 7.1724 | 7.1723 | 7.1722 | 7.1722 | 7.1722 | 7.1722 | 4.8297 | 4.8297 | 4.8303
[5 empty] | LOBI3B_LOBIT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.791 | 11.0701 | 7.3671 | 7.367 | 7.6104 | 7.4907 | 7.4907 | 7.4909 | 7.4909 | 7.4893
[5 empty] | CHAP3-_MIBI3-_1 | 0 | 0 | 0 | 0 | 0.0018917 | 0.0018917 | 0.0018714 | 0.0018714 | 0.50146 | 0.50147 | 0.50106 | 0.50104 | 0.50104 | 0.50104 | 0.50146 | 0.50146 | 0.50109 | 0.50243 | 0.5064 | 11.1793 | 3.353 | 18.587 | 14.1527 | 10.2344 | 9.6183 | 9.6379 | 7.1963 | 7.2146 | 7.2083 | 7.203 | 7.1957 | 7.1958 | 7.1958 | 4.1224 | 4.5319 | 4.5319 | 4.532
[5 empty] | CHAP3-_CHAPX1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5499 | 15.5488 | 11.4755 | 15.6293 | 13.4363 | 11.3685 | 11.1061 | 10.9767 | 10.9768 | 10.9763 | 10.9763 | 10.9782
[5 empty] | CHAP3-_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2101 | 2.2101 | 1.6552 | 1.6552 | 1.1032 | 1.103 | 1.103 | 1.103 | 1.103 | 1.103 | 3.8747 | 5.8371 | 5.8371 | 5.8386
[5 empty] | EWHC3-_MIBI3-_1 | 0 | 0 | 0 | 0 | 0.00038577 | 0.00038577 | 0.00038163 | 0.00038165 | 0.50046 | 0.50046 | 0.50049 | 0.50063 | 0.50063 | 0.50062 | 0.50113 | 0.50113 | 0.50047 | 0.50072 | 0.50231 | 0.51275 | -1.8943 | -1.8729 | -1.8732 | -1.8847 | -2.4826 | -2.4749 | -4.8548 | -4.8475 | -4.8501 | -4.8522 | -4.8551 | -4.855 | -4.855 | -4.8581 | -4.8579 | -4.8579 | -4.8569
[5 empty] | CHAP3-_LOBI3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5839 | 11.4873 | 12.4235 | 9.8719 | 10.1479 | 10.2766 | 10.2766 | 10.2765 | 10.2765 | 10.2772
[5 empty] | GRNA3A_GRNAT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007417 | 0.0074247 | 0.0073487 | 0.0073559 | 0.0074648 | 0.0073185 | 0.007348 | 0.0073929 | 0.0073919 | 0.0073919 | 0.0074677 | 2.3375 | 2.3375 | 2.3369
[5 empty] | ANANT1_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2314 | 12.233 | 9.1469 | 6.0812 | 6.0814 | 6.0816 | 6.0813 | 6.0813 | 6.0818 | 6.0817 | 6.0822 | 6.082 | 6.0819 | 6.1113 | 6.1113 | 6.1113 | 6.1113 | 6.1113 | 6.1113 | 6.1114
[5 empty] | ANANT2_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2334 | 9.1471 | 6.0813 | 6.0815 | 6.0817 | 6.0814 | 6.0814 | 6.0819 | 6.0818 | 6.0823 | 6.0821 | 6.082 | 6.0522 | 6.0522 | 6.0522 | 6.0522 | 6.0522 | 6.0522 | 6.0523
[5 empty] | CHAPX1_LOBI3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5012 | 15.5002 | 11.4493 | 15.5815 | 13.4013 | 11.3437 | 11.0824 | 10.9537 | 10.9537 | 10.9532 | 10.9532 | 10.9551
[5 empty] | CRAG5A_LAHO5-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9716e-08 | -2.2326e-08 | -2.2075e-08 | -2.2111e-08 | -2.2425e-08 | -2.251e-08 | -2.2242e-08 | -2.2326e-08 | -2.24e-08 | -2.2519e-08 | -2.2519e-08 | -2.2519e-08 | -2.2498e-08 | -2.2314e-08 | -2.2314e-08 | -2.2251e-08
[5 empty] | CRAG5B_LAHO5-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9516e-08 | 2.2128e-08 | 2.1873e-08 | 2.191e-08 | 2.2221e-08 | 2.2308e-08 | 2.2039e-08 | 2.2124e-08 | 2.2202e-08 | 2.232e-08 | 2.2317e-08 | 2.2317e-08 | 2.2293e-08 | 2.2108e-08 | 2.2108e-08 | 2.205e-08
[5 empty] | CHAP3-_STCR3-_1 | 0 | 0 | 0 | 0 | -0.0025215 | -0.0025215 | -0.50213 | -0.50213 | -1.0017 | -1.0301 | -1.0306 | -1.0318 | -1.0318 | -1.0928 | -1.1466 | -1.1466 | -1.121 | -13.353 | -25.5963 | -30.0954 | -1.4689 | -16.7015 | -27.18 | -21.6272 | -17.3614 | -28.6171 | -18.9299 | -29.8979 | -29.9436 | -28.6779 | -24.0635 | -24.0772 | -24.0766 | -23.8226 | -23.8514 | -23.8514 | -31.6373
[5 empty] | CHAP3-_MINS3-_1 | 0 | 0 | 0 | 0 | 0.00062978 | 0.00062979 | 0.50026 | 0.50026 | 0.50022 | 0.50022 | 0.50063 | 0.50135 | 0.50135 | 0.50128 | 0.5035 | 0.5035 | 0.50053 | 0.5008 | 0.50572 | 0.50435 | -6.8274 | -6.8277 | -6.8235 | -6.828 | -8.6496 | -8.6433 | -15.8876 | -15.8789 | -15.8825 | -15.8851 | -15.8878 | -15.8877 | -15.8877 | -15.8877 | -15.8879 | -15.8879 | -15.8869
[5 empty] | lne_AL048A_GRNA1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3385e-08 | 4.3385e-08 | 0.06113 | 0.11085 | 0.11085 | 0.090476 | 0.089545 | 0.088773 | 0.088896 | -7.2563 | -7.2576 | -7.2581 | -7.2575 | -9.0898 | -9.0905 | -9.0905 | -9.107 | -9.1071 | -9.1071 | -9.0905 | -9.0905 | -9.0905 | -9.0905 | -9.0905 | -9.0905 | -1.2999
[5 empty] | lne_CHAP1-_AL048A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0163e-05 | 6.0163e-05 | 0.061181 | 0.11124 | 0.11124 | 0.090513 | 0.089554 | 0.088908 | 0.088992 | -7.2502 | -7.2515 | -7.2517 | -7.2514 | -9.0802 | -9.0806 | -9.0806 | -9.0965 | -9.0968 | -9.097 | -9.0806 | -9.0806 | -9.0806 | -9.0806 | -9.0806 | -9.0806 | -1.2987
[5 empty] | lne_EWEH1S_EWEH1R_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028203 | 0.028203 | 0.029617 | 0.029187 | 0.028856 | 0.028906 | -7.3232 | -7.3238 | -7.324 | -7.3238 | -9.1597 | -9.1599 | -9.1599 | -9.1599 | -9.1599 | -9.1599 | -9.1599 | -9.1599 | -9.1599 | -9.1599 | -9.1599 | -9.1599 | -9.1598
Manual/Calculated
|  |  |  | chapelcross33kv | CHAP08_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross33kv | CHAP3-_SOLWAY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | CHAP3A1 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | chapelcross132kv | CHAP3A2 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | chapelcross132kv | CHAP1-_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | chapelcross132kv | CHAP1-_CHAP3-_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | CHAP1-_M1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | chapelcross132kv | CHAP1-_M1-_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | chapelcross132kv | CHAP1-_R1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | HARK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | DUMF-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | ECCF-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | GRNA-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | DUMF-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | ECCF-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | CHAP1-_T1 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | chapelcross132kv | CHAP1-_T2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | GRNA-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | stevenscroft33kv | STCR3- | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | stevenscroft33kv | STCR3-_STCR0G | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | stevenscroft33kv | STCR0G-_2 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | stevenscroft33kv | STCR0G-_1 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | stevenscroft33kv | STRC0G-_STCRLVT | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | stevenscroft33kv | STCR_AUX | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | stevenscroft33kv | STCR_DIESEL | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | minsca33kv | MINS3- | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | minsca33kv | MINS3-_MINSC | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | minsca33kv | MINS0G | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | ewehillwindfarm1 | EWEH3- | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | ewehillwindfarm1 | EWHC3-_EWHC0G_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | ewehillwindfarm1 | EWEH0G | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | gretna132kv | GRNA1-_SGT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | gretna132kv | GRNA1-_SGT2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | gretna132kv | GRNA1-_EWEH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | gretna400kv | GRNA4-_M1-_SGT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | chapelcrossgretna1 | CHAP1-_GRNA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | ewehillgretna | EWEH3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | ewehillgretna | EWEH3-_GRID1A-_WG2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | ewehillwindfarm2 | EWEH0G_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | gretna400kv | HARK4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999
|  |  |  | gretna400kv | GRNA4-_M1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999

## Lines - Reactive Power
Lines - Reactive Power
Results
Lines
[6 empty] | Post black-out | Pre-restoration | Energise Steven's Croft | 1.1 Energise Steven's croft BB (CUSTOMER) | 1.2 Energise Steven's Croft cable to Chapelcross (CHAP) | 2.1 Energise Minsca PoC (MINSCA WF) | 2.2 Energise Minsca WF (CUSTOMER) | 3.1 Energise Ewe Hill 1 PoC (12) | 3.2 Energise Ewe Hill WF (CUSTOMER) | 4.1 Energise Chapelcross Grid 1 132/33kV Trfr (698-10) | 4.2 Energise Chapelcross 132kV M1 BB (698-710) | 4.3 Energise Chapelcross - Gretna 1 132kV circuit (698-1105) | 5.1 Close Gretna CB, energise Gretna 132kV BB (305) | 5.2 Energise Gretna SGT1 400/132kV (780) | 5.3 Energise Gretna - Ewe Hill 2 132kV circuit (805) | 5.4 Energise Ewe Hill 2 WF (GRID 1) | 5.5 Energise Ewe Hill 2 circuits (WG2) | 6.1 Energise Chapelcross - Annan circuit 1 (698-14) | 6.2 Energise Chapelcross - Annan circuit 2 (698-23) | 7.1 Energise Middlebie SWS - Middlebie circuit (780-11) | 8.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 20% MW | 8.2 Energise Middlebie SWS - Langholm circuit 1 (780-14) | 9.1 Energise Chapelcross - Gretna circuit 2 (698-11) | 10.1 Energise Chapelcross - Gretna circuit 1, Langholm 2, Newcastleton (698-21) | 11.1 Minsca WF, Ewe Hill 1 WF, Ewe Hill 2 WF to produce 25% MW | 11.2 Energise Chapelcross -Lockerbie circuit 1 (698-13) | 11.3 Minsca WF, Ewe Hill 1 WF to produce 45% MW | 11.4 Energise Chapelcross -Lockerbie circuit 2 (698-22) | 12.1 Energise Lockerbie - Kirkbank and Moffat 1 (694-13) | 13.1 Energise Lockerbie - Moffat 2 (694-23) | 14.1 Close Annan 11kV bus section (662-01) | 14.2 Close Lockerbie 11kV bus section (679-01) | 14.3 Close Moffat 11kV bus section (683-01) | 14.4 Connect Langholm T2 (676-20) | 14.5 Connect Gretna T1 (673-10) | 15.1 Energise Gretna 400kV B/B from Harker (X605) | 15.2 Connect Transmisison network to Chapelcross DRZ via SGT1 (X510) | Stevens Croft energised | Steven's croft SPD brkr closed and line to Chapelcross energised | Chapelcross 33kV B/B energised | Circuit Minsca WF energised | Circuit to Ewe Hill WF energised | Grid trfr 1 + Chapelcross - Gretna line energised | Gretna 132kV brkr closed | Annan energised | Middelbie energised | Langholm energised | Gretna B energised | GretnaA + Newcastleton | LockerbieA + B | Kirkbank + Moffat A | Moffat B | Restore to normal
[6 empty] | Reactive Power >>> | [36 empty] | 0 | 1,2 | 1,2 | 3,4 | 5.6 | 7,8,9 | 10,11,12,13 | 14,15 | 16,17 | 18 | 19 | 20,21 | 22,23,24 | 25 | 26 | 27,28,29,30,31
|  |  | network | Name | PF Name | Step -2 | Step -1 | Step 0 | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Step 6 | Step 7 | Step 8 | Step 9 | Step 10 | Step 11 | Step 12 | Step 13 | Step 14 | Step 15 | Step 16 | Step 17 | Step 18 | Step 19 | Step 20 | Step 21 | Step 22 | Step 23 | Step 24 | Step 25 | Step 26 | Step 27 | Step 28 | Step 29 | Step 30 | Step 31 | Step 32 | Step 33 | Step 34 | Stage 0 | Stage 1 | Stage 2 | Stage 3 | Stage 4 | Stage 5 | Stage 6 | Stage 7 | Stage 8 | Stage 9 | Stage 10 | Stage 11 | Stage 12 | Stage 13 | Stage 14 | Stage 15
|  |  | chapelcross33kv |  | lne_CHAP1-_HAKB1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | chapelcross33kv |  | CRAG5B_LAHO5-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3377e-14 | -5.1151e-14 | 1.4306e-14 | 1.1287e-14 | 3.1983e-14 | -1.6284e-14 | 3.1633e-14 | 3.7758e-15 | 5.0955e-15 | 1.0494e-14 | -3.0234e-14 | -4.6395e-14 | 4.2979e-14 | -1.6377e-14 | -1.6377e-14 | -4.5903e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2218e-15 | -1.1451e-14 | 3.244e-15 | 1.3082e-14 | 2.6283e-14 | 1.0918e-14 | -8.384e-14
|  |  | chapelcross33kv | CHAPX3_LAHO3B_1 | CHAPX3_LAHO3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12183 | 0.12162 | 0.050163 | 0.050016 | -0.008736 | -0.0092517 | -0.009717 | -0.010426 | -0.01041 | -0.01041 | -0.45102 | -0.45692 | -0.45692 | -0.46475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.123 | -0.0061391 | -0.0089177 | -0.0083695 | -0.48324
|  |  | chapelcross33kv | LOBI3B_MOFTT2_1 | LOBI3B_MOFTT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056986 | -0.21763 | -0.21111 | -0.54168 | -0.54162 | -0.5421 | -0.5421 | -0.54654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067022 | -0.53678
|  |  | chapelcross33kv |  | lne_CHAP1-_DUMF1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | chapelcross33kv | CHAP3-_LOBI3B_1 | CHAP3-_LOBI3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8839 | 2.087 | 1.463 | 0.87378 | 2.334 | 2.1003 | 2.1004 | 2.1 | 2.1 | 2.0966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9445 | 0.88277 | 1.4771 | 2.103
|  |  | chapelcross33kv |  | CHAP3-_CHAPX1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5261 | 3.5218 | 1.9342 | 1.8414 | 1.2262 | 0.81027 | -0.59545 | -0.36221 | -0.36197 | -0.364 | -0.364 | -0.35375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4766 | 1.7563 | 1.1473 | -0.43517
|  |  | chapelcross33kv | CHAPX4_KIBAT1_1 | CHAPX4_KIBAT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.32109 | -0.31597 | -0.28867 | -0.29234 | -0.29192 | -0.2919 | -0.29205 | -0.29205 | -0.2914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.31997 | -0.31265 | -0.29028
|  |  | chapelcross33kv | CHAPX4_MOFTT1_1 | CHAPX4_MOFTT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22148 | 0.080732 | 0.0030051 | 0.0011604 | 0.34365 | 0.34363 | 0.34378 | 0.34378 | 0.3463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22308 | 0.083971 | 0.34243
|  |  | chapelcross33kv | CHAP3-_CHAPX3_1 | CHAP3-_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047023 | 0.047402 | 0.11713 | 0.11744 | 0.1746 | 0.17586 | 0.177 | 0.17873 | 0.17869 | 0.17869 | 0.61695 | 0.95796 | 0.95796 | 0.96401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043098 | 0.16756 | 0.17505 | 0.17371 | 0.98008
|  |  | chapelcross33kv | GRNA3A_GRNAT1_1 | GRNA3A_GRNAT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.4517e-11 | 1.0535e-10 | 2.2015e-10 | 1.9629e-11 | 2.1005e-10 | 6.1115e-11 | 1.6976e-11 | -3.6327e-12 | 6.9121e-11 | -1.2123e-10 | 5.7026e-11 | -0.36198 | -0.36198 | -0.36072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.0565e-11 | 1.7533e-11 | 3.2106e-11 | 1.8757e-10 | -0.35914
|  |  | chapelcross33kv | LOBI3A_LOBIT1_1 | LOBI3A_LOBIT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.145 | 2.1424 | 1.1889 | 0.53272 | 0.53398 | 0.53556 | -0.82657 | -0.91307 | -0.91291 | -0.91428 | -0.91428 | -0.90996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1248 | 0.53449 | 0.52659 | -0.89704
|  |  | chapelcross33kv |  | LAHO3A_LAHOT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8418 | 1.5622 | 0.78787 | 0.78695 | 0.77938 | 0.7773 | 0.7838 | 0.78172 | 0.77985 | 0.77703 | 0.77709 | 0.77709 | 1.0276 | 1.0418 | 1.0418 | 1.0511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1346 | 1.6125 | 0.78213 | 0.78577 | 0.78333 | 0.78556 | 1.0719
|  |  | chapelcross33kv |  | LAHO3B_LAHOT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8471e-15 | -7.2351e-15 | 2.2813e-14 | 3.2659e-15 | -2.6829e-15 | 2.7721e-14 | 6.4203e-15 | 7.3252e-15 | 8.9882e-15 | 2.2412e-15 | -0.47837 | -0.47787 | -0.47787 | -0.48615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.16e-14 | 2.095e-14 | 8.0745e-16 | 6.7202e-15 | -0.50598
|  |  | chapelcross33kv | MIBI3-_MIBIT1_1 | MIBI3-_MIBIT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12721 | -0.2082 | -0.20506 | -0.20183 | -0.20766 | -0.20805 | -0.2051 | -0.206 | -0.2032 | -0.20409 | -0.2049 | -0.20612 | -0.20609 | -0.20609 | -0.20767 | -0.20755 | -0.20755 | -0.20698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13642 | -0.08816 | -0.20095 | -0.20455 | -0.20299 | -0.2034 | -0.20244 | -0.20589
|  |  | chapelcross33kv | GRNA3B_GRNAT2_1 | GRNA3B_GRNAT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2901 | 0.50588 | 0.50432 | 0.01738 | 0.016758 | 0.025733 | 0.022857 | 0.02028 | 0.016384 | 0.016472 | 0.016471 | 0.01652 | 0.10795 | 0.10795 | 0.1077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2979 | 0.49516 | 0.027883 | 0.024716 | 0.02779 | 0.10821
|  |  | chapelcross33kv | MIBI3-_LAHO3A_1 | MIBI3-_LAHO3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2722 | 2.2535 | 1.0602 | 1.0589 | 1.0546 | 1.0514 | 1.0612 | 1.0581 | 1.0553 | 1.051 | 1.0511 | 1.0511 | 1.1159 | 1.1491 | 1.1491 | 1.1587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7541 | 2.3547 | 1.066 | 1.0716 | 1.0605 | 1.0639 | 1.1787
|  |  | chapelcross33kv | LAHO3B_NEWCT1_1 | LAHO3B_NEWCT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14018 | 0.14002 | 0.0736 | 0.07349 | 0.018291 | 0.017924 | 0.017592 | 0.017088 | 0.017099 | 0.017099 | 0.018684 | 0.018861 | 0.018861 | 0.01909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14065 | 0.019994 | 0.018161 | 0.018552 | 0.019505
|  |  | chapelcross33kv | CHAP3-_MIBI3-_1 | CHAP3-_MIBI3-_1 | 0 | 0 | 0 | 0 | -1.0823 | -1.0823 | -1.0707 | -1.0707 | -0.71646 | -0.72067 | -0.43816 | -0.26211 | -0.26211 | -0.27489 | 0.054816 | 0.054816 | -0.47567 | -1.0276 | -1.6849 | -2.9335 | -0.92157 | 0.7078 | -1.6418 | -1.9328 | -1.6763 | -2.5644 | -1.7032 | -2.5223 | -2.2631 | -2.0282 | -1.6684 | -1.6766 | -1.6765 | -1.2102 | -1.2062 | -1.2062 | -1.3689 | 0 | 0 | 0 | 0 | -0.33026 | -0.33917 | -0.34741 | -0.2644 | 0.21168 | 5.9188 | 2.5926 | 0.96526 | -3.013 | -2.5674 | -2.8418 | -1.7897
|  |  | chapelcross33kv | ANANT1_CHAP3-_1 | ANANT1_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80641 | 0.82709 | 0.25641 | -0.059271 | -0.062648 | -0.058608 | -0.06316 | -0.063634 | -0.056741 | -0.057199 | -0.050598 | -0.052712 | -0.054607 | -0.057351 | -0.057286 | -0.057286 | -0.05725 | -0.057559 | -0.057559 | -0.056215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85345 | 0.28164 | -0.048318 | -0.046358 | -0.055567 | -0.048326 | -0.051345 | -0.049086 | -0.053834
|  |  | chapelcross33kv |  | CARU3A_CHAPX1_1 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0635e-14 | -2.0492e-14 | -6.2382e-15 | -5.4715e-15
|  |  | chapelcross33kv | ANANT2_CHAP3-_1 | ANANT2_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84417 | 0.26492 | -0.056494 | -0.05993 | -0.055834 | -0.060449 | -0.060929 | -0.053941 | -0.054405 | -0.047715 | -0.049857 | -0.051779 | -0.05483 | -0.054765 | -0.054766 | -0.054729 | -0.055036 | -0.055036 | -0.053701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87076 | 0.2904 | -0.045404 | -0.043417 | -0.052751 | -0.045425 | -0.048472 | -0.046182 | -0.051335
|  |  | chapelcross33kv | EWEH3-_MIBI3-_1 | EWHC3-_MIBI3-_1 | 0 | 0 | 0 | 0 | -1.0849 | -1.0849 | -1.0732 | -1.0732 | -0.71816 | -0.72239 | -0.43915 | -0.26281 | -0.26281 | -0.27561 | 0.054256 | 0.054256 | -0.47673 | -1.0305 | -1.6919 | -3.3623 | -0.74034 | -4.1425 | -4.157 | -3.0307 | -2.7425 | -3.6418 | -2.6738 | -3.516 | -3.249 | -3.0075 | -2.6382 | -2.6465 | -2.6465 | -2.1608 | -2.1981 | -2.1981 | -2.3721 | 0 | 0 | 0 | 0 | -0.33107 | -0.33999 | -0.34823 | -0.26517 | -0.22625 | -0.20159 | -0.23185 | -0.26962 | -4.0425 | -3.5743 | -3.8575 | -2.8254
|  |  | chapelcross33kv |  | CRAG5A_LAHO5-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1015e-13 | 2.7685e-12 | -1.2612e-12 | 6.618e-12 | -5.7025e-12 | -3.3185e-13 | -3.4268e-13 | -2.2441e-12 | 1.3486e-12 | -3.9847e-12 | 4.3069e-12 | -9.6263e-13 | -7.6103e-12 | -3.2106e-12 | -3.2106e-12 | 1.9034e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.991e-13 | -5.624e-13 | -3.9107e-13 | -1.4209e-12 | 3.2081e-13 | -2.3989e-12 | 6.8414e-12
|  |  | chapelcross33kv | CHAPX4_LOBI3A_1 | CHAPX4_LOBI3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.099606 | 0.23524 | 0.28567 | 0.29118 | -0.051735 | -0.051736 | -0.051733 | -0.051733 | -0.054898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.096888 | 0.22868 | -0.052149
|  |  | chapelcross33kv | CHAPX1_LOBI3A_1 | CHAPX1_LOBI3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4408 | 3.4366 | 1.8882 | 1.7577 | 1.1649 | 0.76678 | -0.63687 | -0.40259 | -0.40236 | -0.40435 | -0.40435 | -0.39423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4807 | 1.7682 | 1.1808 | -0.37923
|  |  | chapelcross33kv | CHAP3-_GRNA3B_1 | CHAP3-_GRNA3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1756 | 0.95694 | 0.95476 | 0.18638 | 0.18549 | 0.1984 | 0.19426 | 0.19056 | 0.18495 | 0.18507 | 0.18507 | 0.18514 | 0.15496 | 0.15496 | 0.15517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2116 | 0.95561 | 0.20825 | 0.19694 | 0.20136 | 0.15669
|  |  | chapelcross33kv | CHAP3-_MINS3-_1 | CHAP3-_MINS3-_1 | 0 | 0 | 0 | 0 | -2.0448 | -2.0448 | -0.83216 | -0.83216 | -1.1121 | -1.1244 | -0.30147 | 0.21143 | 0.21143 | 0.1742 | 1.1348 | 1.1348 | -0.41072 | -2.0183 | -3.9324 | -3.5551 | 0.48568 | -2.1958 | -3.7308 | -1.999 | -1.3312 | -3.9467 | -1.7548 | -4.1876 | -3.4176 | -2.7199 | -1.6514 | -1.6757 | -1.6755 | -1.689 | -1.5741 | -1.5741 | -2.0725 | 0 | 0 | 0 | 0.72548 | 0.72169 | 0.70477 | 0.68914 | 0.84673 | 0.8617 | -4.0201 | -4.7194 | -1.371 | -7.7954 | -2.9262 | -3.7439 | -1.9552
|  |  | chapelcross33kv | CHAP3-_STCR3-_1 | CHAP3-_STCR3-_1 | 0 | 0 | 0 | 0 | 3.1271 | 3.1271 | 1.9028 | 1.9028 | 1.8286 | 1.8268 | 2.3789 | 2.7232 | 2.7232 | 2.7122 | 3.3692 | 3.3692 | 2.3263 | 4.3839 | 6.9292 | 8.7851 | 1.7603 | 3.9913 | 6.3627 | 5.6616 | 4.4467 | 6.399 | 3.278 | 5.3348 | 5.8715 | 5.8848 | 5.0045 | 4.9927 | 4.9926 | 4.8984 | 4.9855 | 4.9855 | 7.4063 | 0 | 5.4094e-14 | 5.4094e-14 | -0.72548 | -0.39144 | 0.6272 | 1.5863 | -1.129 | -0.47715 | -0.59479 | 1.2102 | 1.6921 | 4.8539 | 5.0264 | 5.4769 | 4.9041
|  |  | chapelcross33kv | LOBI3B_LOBIT2_1 | LOBI3B_LOBIT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5746 | 1.4328 | 0.64845 | 0.64686 | 2.0455 | 2.1342 | 2.1342 | 2.1347 | 2.1347 | 2.1339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5885 | 0.64704 | 0.64044 | 2.127
|  |  | chapelcross33kv | CHAP1-_GRNA1 | lne_AL048A_GRNA1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.37506 | -0.37506 | -0.31443 | -1.6667 | -1.6667 | 0.84811 | 0.12555 | -0.7386 | -0.56792 | 0.91706 | -0.28743 | -0.98056 | -0.19873 | 0.011175 | -1.1691 | -1.0918 | -2.2002 | -1.8514 | -1.5358 | -1.0452 | -1.0562 | -1.056 | -1.0621 | -1.0104 | -1.0104 | -2.5624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | chapelcross33kv | CHAP1-_GRNA1 | lne_CHAP1-_AL048A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0315 | -1.0315 | -0.9705 | -2.5009 | -2.5009 | 0.19824 | -0.52126 | -1.3813 | -1.2115 | 0.28556 | -0.91358 | -1.6032 | -0.8253 | -0.60663 | -1.781 | -1.7041 | -2.8062 | -2.4594 | -2.1456 | -1.6577 | -1.6686 | -1.6685 | -1.6746 | -1.6231 | -1.6231 | -3.2002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | chapelcross33kv |  | lne_AL048B_GRNA1-_1 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | 0 | 0 | 0 | 0 | -0.3686 | -1.3036 | -0.80089 | -0.79458 | -0.82307 | -0.81973 | -1.272 | -0.805 | -1.2607 | -0.82438 | -1.2677
|  |  | chapelcross33kv |  | lne_CHAP1-_AL048B_1 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | 0 | 0 | 0 | 0 | 0 | -1.0137 | -1.9563 | -1.1982 | -1.1888 | -1.2314 | -1.2264 | -1.9008 | -1.2044 | -1.884 | -1.2333 | -1.8945
|  |  | chapelcross33kv |  | CHAP08_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.6063e-05 | -6.6932e-05 | -4.0743e-05 | -4.0422e-05 | -4.1871e-05 | -4.1702e-05 | -6.4486e-05 | -4.0952e-05 | -6.3917e-05 | -4.1938e-05 | -6.4272e-05
|  |  | chapelcross33kv | CHAP3-_SOLWAY | CHAP3-_SOLWAY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2312e-27 | 1.4619e-22 | -1.8168e-18 | 5.9067e-19 | -1.5795e-18 | -4.8668e-18 | 1.1058e-19 | 1.0078e-18 | -1.3653e-21 | 2.5534e-18 | -2.2374e-19
|  |  | chapelcross132kv | CHAP3A1 | CHAP3A1 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | chapelcross132kv | CHAP3A2 | CHAP3A2 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | chapelcross132kv | CHAP1-_CHAP3-_1 | CHAP1-_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | chapelcross132kv | CHAP1-_CHAP3-_2 | CHAP1-_CHAP3-_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | chapelcross132kv | CHAP1-_M1-_1 | CHAP1-_M1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | CHAP1-_M1-_2 | CHAP1-_M1-_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | CHAP1-_R1-_1 | CHAP1-_R1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | HARK | HARK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | DUMF-2 | DUMF-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | ECCF-2 | ECCF-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | GRNA-2 | GRNA-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | DUMF-1 | DUMF-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | ECCF-1 | ECCF-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | CHAP1-_T1 | CHAP1-_T1 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | CHAP1-_T2 | CHAP1-_T2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcross132kv | GRNA-1 | GRNA-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STCR3- | STCR3- | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STCR3-_STCR0G | STCR3-_STCR0G | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STCR0G-_2 | STCR0G-_2 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STCR0G-_1 | STCR0G-_1 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STRC0G-_STCRLVT | STRC0G-_STCRLVT | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STCR_AUX | STCR_AUX | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | stevenscroft33kv | STCR_DIESEL | STCR_DIESEL | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | minsca33kv | MINS3- | MINS3- | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | minsca33kv | MINS3-_MINSC | MINS3-_MINSC | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | minsca33kv | MINS0G | MINS0G | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ewehillwindfarm1 | EWEH3- | EWEH3- | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ewehillwindfarm1 | EWEH3-_EWEH0G_1 | EWHC3-_EWHC0G_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ewehillwindfarm1 | EWEH0G | EWEH0G | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | gretna132kv | GRNA1-_SGT1 | GRNA1-_SGT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | gretna132kv | GRNA1-_SGT2 | GRNA1-_SGT2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | gretna132kv | GRNA1-_EWEH | GRNA1-_EWEH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | gretna400kv | GRNA4-_M1-_SGT1 | GRNA4-_M1-_SGT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | chapelcrossgretna1 | CHAP1-_GRNA1 | CHAP1-_GRNA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ewehillgretna | EWEH3 | EWEH3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ewehillgretna | EWEH3-_GRID1A-_WG2 | EWEH3-_GRID1A-_WG2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | ewehillwindfarm2 | EWEH0G_2 | EWEH0G_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | gretna400kv | HARK4 | HARK4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  | gretna400kv | GRNA4-_M1 | GRNA4-_M1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
End of sheet
Lines are on SLD
Not used in simulation
Vlookup
Copy and paste from PF
[5 empty] | lne_CHAP1-_HAKB1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | lne_GRNA1-_JUNV1-_1 | -1.0104e-20 | -1.0104e-20 | 2.8781e-20 | 2.8781e-20 | 2.8781e-20 | 2.8781e-20 | 2.8781e-20 | 2.8781e-20 | 2.8781e-20 | 2.8781e-20 | 2.8781e-20 | 2.8781e-20 | 2.8781e-20 | 2.8781e-20 | -3.9144e-21 | -3.9144e-21 | 2.8781e-20 | 2.8781e-20 | 2.8781e-20 | 2.8781e-20 | 2.8781e-20 | -1.4541e-20 | -1.2175e-21 | -1.6938e-21 | -1.6938e-21 | 9.8074e-21 | -4.8451e-20 | 4.4918e-20 | 1.9474e-20 | 4.2443e-20 | -6.135e-21 | 2.0371e-20 | 2.0371e-20 | 2.8781e-20 | 2.8781e-20 | 4.5129e-20 | 5.3259e-20
[5 empty] | lne_CHAP1-_DUMF1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | MIBI3-_LAHO3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2722 | 2.2535 | 1.0602 | 1.0589 | 1.0546 | 1.0514 | 1.0612 | 1.0581 | 1.0553 | 1.051 | 1.0511 | 1.0511 | 1.1159 | 1.1491 | 1.1491 | 1.1587
[5 empty] | CHAPX4_LOBI3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.099606 | 0.23524 | 0.28567 | 0.29118 | -0.051735 | -0.051736 | -0.051733 | -0.051733 | -0.054898
[5 empty] | CHAP3-_GRNA3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1756 | 0.95694 | 0.95476 | 0.18638 | 0.18549 | 0.1984 | 0.19426 | 0.19056 | 0.18495 | 0.18507 | 0.18507 | 0.18514 | 0.15496 | 0.15496 | 0.15517
[5 empty] | CHAPX4_KIBAT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.32109 | -0.31597 | -0.28867 | -0.29234 | -0.29192 | -0.2919 | -0.29205 | -0.29205 | -0.2914
[5 empty] | CHAPX4_MOFTT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22148 | 0.080732 | 0.0030051 | 0.0011604 | 0.34365 | 0.34363 | 0.34378 | 0.34378 | 0.3463
[5 empty] | LAHO3A_LAHOT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8418 | 1.5622 | 0.78787 | 0.78695 | 0.77938 | 0.7773 | 0.7838 | 0.78172 | 0.77985 | 0.77703 | 0.77709 | 0.77709 | 1.0276 | 1.0418 | 1.0418 | 1.0511
[5 empty] | MIBI3-_MIBIT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12721 | -0.2082 | -0.20506 | -0.20183 | -0.20766 | -0.20805 | -0.2051 | -0.206 | -0.2032 | -0.20409 | -0.2049 | -0.20612 | -0.20609 | -0.20609 | -0.20767 | -0.20755 | -0.20755 | -0.20698
[5 empty] | LAHO3B_LAHOT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8471e-15 | -7.2351e-15 | 2.2813e-14 | 3.2659e-15 | -2.6829e-15 | 2.7721e-14 | 6.4203e-15 | 7.3252e-15 | 8.9882e-15 | 2.2412e-15 | -0.47837 | -0.47787 | -0.47787 | -0.48615
[5 empty] | CHAPX3_LAHO3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12183 | 0.12162 | 0.050163 | 0.050016 | -0.008736 | -0.0092517 | -0.009717 | -0.010426 | -0.01041 | -0.01041 | -0.45102 | -0.45692 | -0.45692 | -0.46475
[5 empty] | LAHO3B_NEWCT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14018 | 0.14002 | 0.0736 | 0.07349 | 0.018291 | 0.017924 | 0.017592 | 0.017088 | 0.017099 | 0.017099 | 0.018684 | 0.018861 | 0.018861 | 0.01909
[5 empty] | LOBI3A_LOBIT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.145 | 2.1424 | 1.1889 | 0.53272 | 0.53398 | 0.53556 | -0.82657 | -0.91307 | -0.91291 | -0.91428 | -0.91428 | -0.90996
[5 empty] | LOBI3B_MOFTT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056986 | -0.21763 | -0.21111 | -0.54168 | -0.54162 | -0.5421 | -0.5421 | -0.54654
[5 empty] | GRNA3B_GRNAT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2901 | 0.50588 | 0.50432 | 0.01738 | 0.016758 | 0.025733 | 0.022857 | 0.02028 | 0.016384 | 0.016472 | 0.016471 | 0.01652 | 0.10795 | 0.10795 | 0.1077
[5 empty] | LOBI3B_LOBIT2_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5746 | 1.4328 | 0.64845 | 0.64686 | 2.0455 | 2.1342 | 2.1342 | 2.1347 | 2.1347 | 2.1339
[5 empty] | CHAP3-_MIBI3-_1 | 0 | 0 | 0 | 0 | -1.0823 | -1.0823 | -1.0707 | -1.0707 | -0.71646 | -0.72067 | -0.43816 | -0.26211 | -0.26211 | -0.27489 | 0.054816 | 0.054816 | -0.47567 | -1.0276 | -1.6849 | -2.9335 | -0.92157 | 0.7078 | -1.6418 | -1.9328 | -1.6763 | -2.5644 | -1.7032 | -2.5223 | -2.2631 | -2.0282 | -1.6684 | -1.6766 | -1.6765 | -1.2102 | -1.2062 | -1.2062 | -1.3689
[5 empty] | CHAP3-_CHAPX1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5261 | 3.5218 | 1.9342 | 1.8414 | 1.2262 | 0.81027 | -0.59545 | -0.36221 | -0.36197 | -0.364 | -0.364 | -0.35375
[5 empty] | CHAP3-_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047023 | 0.047402 | 0.11713 | 0.11744 | 0.1746 | 0.17586 | 0.177 | 0.17873 | 0.17869 | 0.17869 | 0.61695 | 0.95796 | 0.95796 | 0.96401
[5 empty] | EWHC3-_MIBI3-_1 | 0 | 0 | 0 | 0 | -1.0849 | -1.0849 | -1.0732 | -1.0732 | -0.71816 | -0.72239 | -0.43915 | -0.26281 | -0.26281 | -0.27561 | 0.054256 | 0.054256 | -0.47673 | -1.0305 | -1.6919 | -3.3623 | -0.74034 | -4.1425 | -4.157 | -3.0307 | -2.7425 | -3.6418 | -2.6738 | -3.516 | -3.249 | -3.0075 | -2.6382 | -2.6465 | -2.6465 | -2.1608 | -2.1981 | -2.1981 | -2.3721
[5 empty] | CHAP3-_LOBI3B_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8839 | 2.087 | 1.463 | 0.87378 | 2.334 | 2.1003 | 2.1004 | 2.1 | 2.1 | 2.0966
[5 empty] | GRNA3A_GRNAT1_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.4517e-11 | 1.0535e-10 | 2.2015e-10 | 1.9629e-11 | 2.1005e-10 | 6.1115e-11 | 1.6976e-11 | -3.6327e-12 | 6.9121e-11 | -1.2123e-10 | 5.7026e-11 | -0.36198 | -0.36198 | -0.36072
[5 empty] | ANANT1_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80641 | 0.82709 | 0.25641 | -0.059271 | -0.062648 | -0.058608 | -0.06316 | -0.063634 | -0.056741 | -0.057199 | -0.050598 | -0.052712 | -0.054607 | -0.057351 | -0.057286 | -0.057286 | -0.05725 | -0.057559 | -0.057559 | -0.056215
[5 empty] | ANANT2_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84417 | 0.26492 | -0.056494 | -0.05993 | -0.055834 | -0.060449 | -0.060929 | -0.053941 | -0.054405 | -0.047715 | -0.049857 | -0.051779 | -0.05483 | -0.054765 | -0.054766 | -0.054729 | -0.055036 | -0.055036 | -0.053701
[5 empty] | CHAPX1_LOBI3A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4408 | 3.4366 | 1.8882 | 1.7577 | 1.1649 | 0.76678 | -0.63687 | -0.40259 | -0.40236 | -0.40435 | -0.40435 | -0.39423
[5 empty] | CRAG5A_LAHO5-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1015e-13 | 2.7685e-12 | -1.2612e-12 | 6.618e-12 | -5.7025e-12 | -3.3185e-13 | -3.4268e-13 | -2.2441e-12 | 1.3486e-12 | -3.9847e-12 | 4.3069e-12 | -9.6263e-13 | -7.6103e-12 | -3.2106e-12 | -3.2106e-12 | 1.9034e-12
[5 empty] | CRAG5B_LAHO5-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3377e-14 | -5.1151e-14 | 1.4306e-14 | 1.1287e-14 | 3.1983e-14 | -1.6284e-14 | 3.1633e-14 | 3.7758e-15 | 5.0955e-15 | 1.0494e-14 | -3.0234e-14 | -4.6395e-14 | 4.2979e-14 | -1.6377e-14 | -1.6377e-14 | -4.5903e-14
[5 empty] | CHAP3-_STCR3-_1 | 0 | 0 | 0 | 0 | 3.1271 | 3.1271 | 1.9028 | 1.9028 | 1.8286 | 1.8268 | 2.3789 | 2.7232 | 2.7232 | 2.7122 | 3.3692 | 3.3692 | 2.3263 | 4.3839 | 6.9292 | 8.7851 | 1.7603 | 3.9913 | 6.3627 | 5.6616 | 4.4467 | 6.399 | 3.278 | 5.3348 | 5.8715 | 5.8848 | 5.0045 | 4.9927 | 4.9926 | 4.8984 | 4.9855 | 4.9855 | 7.4063
[5 empty] | CHAP3-_MINS3-_1 | 0 | 0 | 0 | 0 | -2.0448 | -2.0448 | -0.83216 | -0.83216 | -1.1121 | -1.1244 | -0.30147 | 0.21143 | 0.21143 | 0.1742 | 1.1348 | 1.1348 | -0.41072 | -2.0183 | -3.9324 | -3.5551 | 0.48568 | -2.1958 | -3.7308 | -1.999 | -1.3312 | -3.9467 | -1.7548 | -4.1876 | -3.4176 | -2.7199 | -1.6514 | -1.6757 | -1.6755 | -1.689 | -1.5741 | -1.5741 | -2.0725
[5 empty] | lne_AL048A_GRNA1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.37506 | -0.37506 | -0.31443 | -1.6667 | -1.6667 | 0.84811 | 0.12555 | -0.7386 | -0.56792 | 0.91706 | -0.28743 | -0.98056 | -0.19873 | 0.011175 | -1.1691 | -1.0918 | -2.2002 | -1.8514 | -1.5358 | -1.0452 | -1.0562 | -1.056 | -1.0621 | -1.0104 | -1.0104 | -2.5624
[5 empty] | lne_CHAP1-_AL048A_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0315 | -1.0315 | -0.9705 | -2.5009 | -2.5009 | 0.19824 | -0.52126 | -1.3813 | -1.2115 | 0.28556 | -0.91358 | -1.6032 | -0.8253 | -0.60663 | -1.781 | -1.7041 | -2.8062 | -2.4594 | -2.1456 | -1.6577 | -1.6686 | -1.6685 | -1.6746 | -1.6231 | -1.6231 | -3.2002
[5 empty] | lne_EWEH1S_EWEH1R_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046522 | 0.046522 | -2.1105 | -1.383 | -0.51242 | -0.68441 | -2.1568 | -0.9438 | -0.24528 | -1.0332 | -1.2328 | -0.043264 | -0.12122 | 0.98013 | 0.62812 | 0.30984 | -0.16818 | -0.15714 | -0.15725 | -0.1511 | -0.20331 | -0.20331 | -0.90514
Manual/Calculated
|  |  |  | chapelcross33kv | CHAP08_CHAPX3_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross33kv | CHAP3-_SOLWAY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | CHAP3A1 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | chapelcross132kv | CHAP3A2 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | chapelcross132kv | CHAP1-_CHAP3-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | chapelcross132kv | CHAP1-_CHAP3-_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | CHAP1-_M1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | chapelcross132kv | CHAP1-_M1-_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | chapelcross132kv | CHAP1-_R1-_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | HARK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | DUMF-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | ECCF-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | GRNA-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | DUMF-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | ECCF-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | CHAP1-_T1 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | chapelcross132kv | CHAP1-_T2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | chapelcross132kv | GRNA-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | stevenscroft33kv | STCR3- | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | stevenscroft33kv | STCR3-_STCR0G | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | stevenscroft33kv | STCR0G-_2 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | stevenscroft33kv | STCR0G-_1 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | stevenscroft33kv | STRC0G-_STCRLVT | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | stevenscroft33kv | STCR_AUX | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | stevenscroft33kv | STCR_DIESEL | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | minsca33kv | MINS3- | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | minsca33kv | MINS3-_MINSC | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | minsca33kv | MINS0G | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | ewehillwindfarm1 | EWEH3- | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | ewehillwindfarm1 | EWHC3-_EWHC0G_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | ewehillwindfarm1 | EWEH0G | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | gretna132kv | GRNA1-_SGT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | gretna132kv | GRNA1-_SGT2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | gretna132kv | GRNA1-_EWEH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | gretna400kv | GRNA4-_M1-_SGT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | chapelcrossgretna1 | CHAP1-_GRNA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | ewehillgretna | EWEH3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | ewehillgretna | EWEH3-_GRID1A-_WG2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | ewehillwindfarm2 | EWEH0G_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
|  |  |  | gretna400kv | HARK4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999 | 999
|  |  |  | gretna400kv | GRNA4-_M1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 999